## Slide 1: EXCRETA DISPOSAL in EMERGENCIES
A service, not just an infrastructure

## Slide 2: Foreword
This manual aims to help you find your way around excreta disposal systems wherever your curiosity leads you. Next you will find the main page where you can click on any topic to go directly to the sections and sub-sections that interest you. In each section a menu on the left side lists links to the manual’s chapters. For any subchapter that contains more than one page you will find navigation arrows on the top right side of the page.
At the bottom of each page, you will find the references used and if it is available on the web a hyperlink has been added for you to reach and consult the original document. You are encouraged to click on the reference titles to open the hyperlinks and look at the documents to find further information.
Authors: Andy Bastable & Laurence Hamai
with inputs from Raissa Azzalini, Zulfiquar Ali Haider, Frederick Komakech and other Oxfam colleagues’ resources whose products can be found in https://www.oxfamwash.org/en
Enjoy your reading

## Slide 3
Excreta disposal system
Consultation
Modalities of implementation
Desludging
Treatment
Adaptation for easier access
Assessment
Monitoring
Main page
Operation & maintenance
Continuity of service
Final disposal
Latrine superstructure
Slab
Storage / pre-treatment pit
Annexes

## Slide 4
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Process to select the most appropriate technologies
Annexes
Step 1
Conduct rapid needs assessment (including users’ consultation) and mapping of the settlement area. 7 key important social and physical factors in deciding which technology /design to use
Step 2
Step 3
Apply decision tree for sanitation design including materials available and how the latrine will be desludged to identify the most appropriate sustainable design latrine
Step 4
Rapidly construct latrines then get feedback on their use and modify accordingly (Sani Tweaks approach)
Step 7
Determine implementation modalities for the treatment facility (by contractor or not; with or without local authorities /utility) and implement the agreed treatment design
Step 8
Implement a monitoring and tracking feedback from the users – Continue consultation. Improve the quality based on the feedbacks and meet users’ expectations
Step 5
Step 6
Consult with local authorities and utilities to determine the most appropriate treatment options and end-product market, design parameters (e.g., site location, skillset, operation and maintenance requirement)
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Design and implement a system for keeping the latrines clean and in good repair
Design the desludging modality and whether a centralized or decentralized faecal sludge treatment plant is necessary

## Slide 5
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Excreta disposal system
Monitoring
Main page
Technology choices
A complete excreta disposal system doesn’t stop at the latrine, whether communal in a camp or familial in household compound. It also includes a desludging / transportation service and an off-site treatment and final disposal site. Various technical options are available for each component of the sanitation service chain. The next page shows a table of suitable options according to the emergency phase.
Annexes
Technology choices
Page 1/2
If you don’t consider the other components of the excreta disposal system when you design your latrine then your sanitation service stops once the latrine pit is full.
Decision tree
Latrine choices
Transport choices
Design spec
Assessment
Treatment choices
If you don’t consult users and service’s stakeholders, you compromise the long-term sustainability of the system.
Household
User interface
Collection / Storage
Treatment
Manual / mechanical desludging & transport or sewers
Transport
Use / Disposal
Reference: Compendium of Sanitation Technologies in Emergencies and GWC – FSM TWIG – Terminology Factsheet

## Slide 6
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Technology choices
Reference “Compendium of sanitation technologies in Emergencies”
Annexes
Page 2/2
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices

## Slide 7
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Decision tree
Technology choices
Is the soil stable or unstable? Is there enough space to build new pit to replace full latrine or will the pit need to be desludged? This will determine is the pit is lined (unstable soil and /or desludging operation) or unlined (stable soil and no desludging)
Excavate?
Raised above ground structures to be built
Pits / subsurface structures to be built
Yes
No
Raised Direct Drop Toilet
Subsurface Direct Drop Toilet
Subsurface Offset Toilet
Raised Offset Toilet
Flood prone / water table < 1.5 m
Yes
No
Is there water or not? This will determine if the toilet is direct drop (no water) or offset (with water)
On-site toilet choice will depend on excavation, water table level and the space available
Annexes
Decision tree for latrine
Page 1/2
Latrine choices
Transport choices
Design spec
Treatment choices

## Slide 8
Decision tree for treatment and desludging service
Page 2/2
There isn’t a simple decision tree to select technology options for desludging and treatment . For similar settings, it’s possible to make different selections based on what services are already available and what has been pre-positioned in contingency stock. However, there are some questions that will help you decide:
Is there desludging services available, mechanical or manual?
Desludging service
Treatment service
How accessible are latrines in the target area for trucks, for smaller mechanical system?
What daily volume of faecal sludge is collected and needs treatment?
What is the viscosity of the sludge and what is the farthest distance and height for pumping out?
How scattered are the target latrines and what is the average distance for transport?
Does the desludging system available required transport capacity and / or transfer stations?
What are the local hydrogeological conditions and contamination risks? Are there local standards that need to be adhered to? Which treatment parameters (BOD, COD, E-Coli, N, P, pH, need to be monitored and treatment standard met?
Will construction licence and environmental survey be required?
Is there an existing treatment facility and how far from the area of intervention?
Is there land available for building a centralised / semi-centralised treatment plant onsite or offsite and with which surface?
What is the topography like and where can effluent be discharged? Does this location impose additional treatment requirement for the effluent?
Is there a market for faecal sludge treatment output, i.e fuel briquette, gas, dry sludge, compost, slurry from biodigestor, biomass?
Is several decentralised treatment stations more efficient than one centralised / semi-centralised treatment plant (in term of CAPEX / OPEX, speed of construction, long term sustainability or integration with local sanitation plan)?
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Decision tree
Technology choices
Annexes
Latrine choices
Transport choices
Design spec
Treatment choices
What is the level of technical expertise available?

## Slide 9
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
COVERAGE:
Sphere Standard: Maximum of 20 people per latrine. (In initial phase aim for 50 p/p/latrine) Trench latrines: maximum of 100 people per 3.5m length of trench at 1m deep and 300mm wide. Separate toilets may need to be provided for men and women – distance to be determined following consultation with women. Ensure disabled toilets and facilities for children
POSITION:
Toilets should be no more than 50m from dwellings. Pit latrines should be a minimum of 6m from dwellings. Latrines should be at least 30m from any ground water sources. Latrines should be available in public places such as markets, health centres & food/non-food distribution points.
PIT DEPTH
The bottom of the latrine should be at least 1.5m above the water table. In fine unsaturated soils and unconsolidated strata within 1.5m virtually all bacteria, viruses and other faecal organisms are removed. This distance will increase in large grained soils, gravels or fissured rock.
ACCUMULATION RATES (approx.)
Solids: 0.5 Litres/person/day in emergencies (0.04 - 0.15m3/person/year in stable situations) Liquid: 0.8 Litres/person/day where water is not used for anal cleansing (approx.) If water is used for anal cleansing the design figure is 1.3 l/p/d. In the initial phase, before wash areas are constructed, people may wash in latrines in which case the figure could be 8 – 10 l/p/d
OTHER:
Ensure locks for doors. All doors should have a functioning locking mechanism. Security lighting may also be necessary. Provide handwashing facilities and if necessary, water or other materials for anal cleansing. Special rails may also be needed to assist the disabled and elderly.
Children’s And Infant’s Excreta
Children under five often make up a significant proportion of the population in many poorer countries – up to 20% in some instances. It is therefore important that ways are also found to dispose of their excreta safely. This issue must be discussed with mothers, especially to identify whether nappies, potties or specially designed latrines will be necessary
Annexes
Design parameters and specifications
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices

## Slide 10
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Sub Surface Direct drop toilet (Excavate)
Annexes
Shallow trench latrine
Deep trench latrine
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 1/7
Treatment choices
Latrine choices
Will users feel safe to use these structures? Ensure your consultation process include feedback from women and girls, children and people with mobility issues.

## Slide 11
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Sub Surface Direct drop toilet (Excavate)
Annexes
Single pit latrine
Single ventilated improved pit (VIP)
Twin Pits Dry System
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 2/7
Treatment choices
Fossa alterna
Double VIP

## Slide 12
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Sub Surface offset toilet (Excavate + Water)
Annexes
Twin Pits for Pour Flush
Worm-Based Toilet (Emerging Technology)
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 3/7
Treatment choices
Will you find appropriate worm locally and will users accept handling wermicompost?

## Slide 13
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Sub Surface offset toilet (Excavate + Water)
Annexes
Septic Tank
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 4/7
Treatment choices
Effluent still contain contaminants and needs to be discharged either through a sewer or through a percolation field. How much space is available, and would user want to reuse effluent for irrigation? (meaning an additional step for effluent treatment will be required to reduce contamination risks or discouraging the idea)?

## Slide 14
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Raised direct drop toilet
Annexes
Raised Latrine
Double Vault UDDT
(Urine Diversion Dehydration Toilet)
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 5/7
Treatment choices
Consult with users to ensure they will feel comfortable emptying the stabilised dry sludge

## Slide 15
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Raised direct drop toilet
Annexes
Container-Based Toilet
Chemical Toilet
Reference: Compendium of Sanitation Technologies in Emergencies
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 6/7
Treatment choices
Appropriate in places where there is little space, or where people are mostly renting their accommodation
Consult with users to ensure there is an appropriate system to collect, transport and safely disposed of bag (or clean containers)

## Slide 16
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Raised offset toilet (Water)
Annexes
Raised Pour Flush
Biofil Toilet
It is both a containment and a treatment technology. The system is composed of a pour flush interface, followed by a composting part were solids and liquid are separated. Microorganisms degrade matter through aerobic decomposition in enclosed container (Biofilcom, 2017)
Worm-Based Toilet
Technology choices
Decision tree
Transport choices
Design spec
Latrine choices
Page 7/7
Treatment choices

## Slide 17
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Design spec
Transport choices
Reference: Compendium of Sanitation Technologies in Emergencies
Page 1/2
Manual emptying and transport
Motorised emptying and transport
Treatment choices
Transport choices

## Slide 18
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Treatment choices
Design spec
Transport choices
Reference: Compendium of Sanitation Technologies in Emergencies
Page 2/2
Simplified sewer
Conventional gravity sewer
Mobilisation and promotion is required to minimise pipe blockage and facilitate proper maintenance. Prior consultation will be used to determine an appropriate O&M mechanism

## Slide 19
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Page 1/9
A treatment plant is constituted of different treatment steps, each with various choices.
Pre-treatment
Post treatment
Primary treatment
Secondary treatment
Tertiary treatment
Eliminate grit and solid waste to protect equipment (pump, pipe) and ensure the quality of end product
Blackwater Greywater Faecal sludge
Sludge
Effluent
Effluent
Dry sludge
Biomass
Biogas
Compost
Dewatering and concentration of sludge to reduce the size of the secondary treatment infrastructure
Anaerobic Treatment
Aerobic treatment (may require compressor to inject air / oxygen)
Mixed aerobic and anaerobic treatment
Chemical or physical Treatment
This stage depend on environment sensitivity, local regulations and standards, for reuse and / or disposal compared to the quality of output from the secondary treatment
Treatment choices
Organic matter (BOD, TDS, TSS) and nutrient reduction and / or transformation, pathogen removal are various objectives achieved by the different treatment structures
Fuel briquette manufacturing
Co-composting
Producing swimming water quality effluent
Physical Treatment
Physical Treatment
Wastewater and faecal sludge generated by medical centres and factories may contain metallic and other pollutant requiring specific treatment whose end products may not be eligible for reuse.
Initial consultation with users is required to ensure the quality and reuse of treatment outputs fit into the local circular economy and match population needs.

## Slide 20
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Page 2/9
Pre-Treatment
Pre- and Post treatment
Post-Treatment

## Slide 21
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Settler
Primary treatment
Sedimentation and thickening ponds
Page 3/9

## Slide 22
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Secondary treatment
Activated Sludge
Trickling Filter
Need pre- and primary treatment to operate correctly
Mostly aerobic reactions with pockets of anaerobic conditions
Aerobic treatment process
Page 4/9

## Slide 23
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Anaerobic Filter
Anaerobic Baffled Reactor (ABR)
Need pre-treatment to operate correctly
Page 5/9
First chamber acts as primary treatment

## Slide 24
Co-composting
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Vermicomposting and vermifiltration
Need pre-treatment to eliminate plastic and other non-organic solids
Aerobic treatment processes
Page 6/9
Local taboo in handling sanitation by-product from faecal sludge may apply to the resulting compost. Consult with users to identify such issues

## Slide 25
Unplanted Drying Beds
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Planted Drying Beds
Aerobic treatment process
Dry sludge and leachate need further treatment (e.g. respectively co-composting and waste stabilisation pond)
Dry sludge needs removal every 10-15 days
Dry sludge need removal every 3-5 years
Plan several beds to alternate and maintain operation
Sludge applied every 3-7 days
Leachate needs further treatment (e.g. horizontal flow constructed wetland).
Sludge may require pre-treatment
Page 7/9

## Slide 26
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Biogas Reactor
Hydraulic retention time will depend on temperature and pathogenic risk of sludge and varies from 15 to 60 days
Effluent and digestate (produced daily) may require further treatment if reuse in agriculture or if aquifer contamination risks are high
Page 8/9
Hydrated Lime Treatment

## Slide 27
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Excreta disposal system
Monitoring
Main page
Annexes
Technology choices
Decision tree
Latrine choices
Transport choices
Design spec
Treatment choices
Reference: Compendium of Sanitation Technologies in Emergencies
Treatment of effluent and wastewater
Constructed Wetland
Mixed Aerobic and anaerobic treatment process
Waste Stabilisation Ponds
Page 9/9

## Slide 28
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Assessment
Monitoring
Excreta disposal system
Main page
What are local practices?
  How did people dispose of excreta before the crisis,
  What are they doing now & what would they find acceptable now,
  Is water available e.g pour flush versus direct drop,
  Religious/cultural habits,
  Sharing preferences,
  And anal cleansing practice?
Location; which locations are possible given soil and topography and what is socially acceptable?
Can you excavate? The importance of soil type – rocky, very hard, very soft sand to be determine.
What is the space available? Are the affected population densely packed or spread out? E.g., design for desludging or re-digging pits. Where would desludged material go?
What is the ground permeability? Infiltration capacity of the soil to determine ground conditions.
Where is the water table level? i.e., groundwater considerations regarding contamination and whether underground structures might flood during seasonal fluctuations.
What is present capacity? Are there current facilities, sewage system that can be repaired or connected too?
7 rapid questions before starting latrine building
Mapping of the settlement area for latrine construction
Mapping of the nature of the settlement area in view of the suitability for construction of specific type of latrine is an important step towards making the right decision for latrine design options.
In formal settlements such as refugee camps, with designated locations for latrines, mapping should focus on flooding during the rainy season, the groundwater level in dry and rainy seasons, whether the soil can be excavated (e.g. whether subsurface conditions are rocky) and whether the subsoil is collapsible when wet.
The findings of the mapping will inform which kinds of latrine technology will be appropriate in the settlement (or in parts of the settlement). This will provide important information in planning and the O&M aspects of the sanitation program.
Annexes
These questions need answers even in a rapid onset emergency

## Slide 29
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Access Issues
SaniTweak
Community engagement
Annexes
If latrines aren’t used, money, time and resources are wasted and we are failing in our responsibility to the communities we work with.
CPT

## Slide 30
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Access Issues
SaniTweak
Community engagement
Recent research from humanitarian responses shows that on average 40% of women are not using the latrines provided.
People with mobility issues may face difficulty using a toilet
Not only young children can be afraid to use a toilet. Even a 6-year old child can fall through a 25cm diameter latrine hole
The main reasons stated are:
Annexes
Access Issues
Not wanting to be seen going to the toilet
CPT
Ensure you listen to all users to understand barriers and adapt your design
Lack of cleanliness

## Slide 31
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Community engagement
Access Issues
SaniTweak
Annexes
Reference: Oxfam – An introduction to Community Engagement in WASH
Page 1/4
Community engagement in WASH is a planned and dynamic process to connect communities and other emergency response stakeholders to increase community’s control over the impact of the response. It brings together the capacities and perspectives of communities and responders.
Community Engagement in WASH video
CPT
Community Engagement

## Slide 32
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Community engagement
Access Issues
SaniTweak
Annexes
Reference: Oxfam – An introduction to Community Engagement in WASH
Page 2/4
CPT
Tools like Sani Tweak and the Community Perception Tracker (CPT) will help better engage communities in the process of designing, building and maintaining an excreta disposal service
Each step in which WASH Engineers participate will facilitate the design, implementation, and operation & maintenance of an appropriate excreta disposal service
WASH Engineers should consider Community Engagement as a high return investment to ensure the success of their project.

## Slide 33
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Community engagement
Access Issues
SaniTweak
Annexes
The context also play its part: what is possible in a conflict situation may be different from opportunities in a protracted crisis or natural disaster.
Ask yourself: Where is my programme in this continuous process ... and can we hand over more control to communities?
Page 3/4
CPT
Community engagement enables people to have a say in decision making wherever possible.
Different levels of engagement may be practical or appropriate at different stages in the response – or they may happen simultaneously.

## Slide 34
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Community engagement
Access Issues
SaniTweak
Annexes
Page 4/4
CPT
Understanding enablers and motivators can inform latrine design
As part of the community engagement process, hygiene promoters will go through a 5 step process for designing activities to change behaviour and practices regarding public health risks, including excreta disposal and handwashing with soap.
WASH engineers need to pay attention to two of these steps as they can influence and improve the design of an excreta disposal system
Understanding taboo in handling faecal sludge treatment by-products will influence both treatment design and operation and maintenance systems
Improving agriculture or energy production as a by-product of faecal sludge treatment could be a motivator for both latrine uptake and long-term sustainability of the excreta disposal system
Design options for the excreta disposal system will influence any plan and activity to change behaviour and practices

## Slide 35
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
SaniTweak
Access Issues
Community engagement
Annexes
Page 1/4
The goal
Sani Tweaks’ aim is to ensure that, before the superstructure is designed, even in rapid onset emergencies, appropriate consultation with potential users happens.
Consult
Modify the design
Consult again
CPT
SaniTweak

## Slide 36
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
SaniTweak
Access Issues
Community engagement
Annexes
Sani Tweaks – What does it means?
Have a system in place for gathering feedback whilst the latrine is in use, and for ongoing repairs - particularly if the latrine is made of plastic sheeting. How will the latrines be kept clean, and how will they be desludged or replaced?
Consult
Before starting a latrine building programme, consult the users: what are their practices, preferences, minimum distance between men's and women's toilets, vulnerable people's needs, children and babies' needs, menstrual hygiene management needs, siting constraints.
Modify
Change both the design of the latrine, and the sanitation programme, and keep changing it as the programme continues. Consider lighting, door locks, accessibility, privacy, wall height, wall material, doors, male/female segregation, screens, adaptations for the disabled and elderly, child-specific latrines, sanitary pad reuse/drying or disposal facilities, handwashing facilities and handwashing motivators.
Consult again
Consult
Modify the design
Consult again
Page 2/4
CPT

## Slide 37
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
SaniTweak
Access Issues
Community engagement
Annexes
Sani Tweaks - Best Practices in Sanitation
Page 3/4
CPT
See Sani Tweak video

## Slide 38
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
SaniTweak
Access Issues
Community engagement
Annexes
The following resources provide guidance, in a variety of formats to suit different needs, onhow to conduct such continuous consultation with the community:
Sani Tweaks Resources
Checklist
Booklet
Page 4/4
Find out more at
https://www.oxfamwash.org/sanitweaks
CPT

## Slide 39
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Access Issues
SaniTweak
Community engagement
Annexes
CPT
Community Perception Tracker - CPT
Find out more at: https://www.oxfamwash.org/en/communities/community-perception-tracker
The CPT is an approach that uses a mobile tool to enable staff to capture, analyse and understand the perceptions of communities during disease outbreaks. Correlated with epidemiological data, it is used to inform and adjust programming, and provide an evidence base for advocacy and influencing
Page 1/2
The CPT is a vital part of Oxfam’s Community Engagement approach.

## Slide 40
Consultation
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Monitoring
Excreta disposal system
Assessment
Main page
Access Issues
SaniTweak
Community engagement
Annexes
CPT
Page 2/2
How is the CPT relevant to the work of engineers?
If the CPT is in place in your country of operation, contact the team in charge to use it and to get information in order to attune to communities
The CPT can give information on the context, some of which may be useful for adapting design, operation and maintenance approaches
The CPT provide insight on what is a priority for communities
When participating in the CPT, you learn to listen completely to community members without the boundary of your program
The CPT is like a temperature check. It give you a sense of perception trends within the communities.
From the trends analysis, you can identify what questions need further in-depth research (through focus group discussion for example)
The CPT is real time and documented
The CPT provides only qualitative insight

## Slide 41
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Monitoring
Monitoring is the systematic and continuous process of collecting and using information throughout the programme cycle for the purpose of management and decision-making. WASH programmes should include:
Process monitoring that looks at how the project is being developed.
Impact monitoring that looks at whether the project is having the intended impact.
Process
Impact
MEAL responsibility with WASH team inputs
WASH team responsibility
Indicators

## Slide 42
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Process monitoring (continuous process - checklist)
Page 1/3
To verify design specifications are respected and are maintained as long as the service is needed
Stick with 50cm and 1m marks, lower to the top of the faeces in the pit
50cm mark visible, the pit is overfilled
1m mark visible, plan for desludging or digging a new pit as replacement
Check water doesn’t stay on the roof
Check water falling from the roof is drained out and doesn’t dig under the slab
Check the inside lock always function
Check the walls are not see-through
Check inside the slab is clean
Check the pit is not full
Check the slab and latrine are not collapsing or at risk to collapse
Functional latrine
Check there is a functioning handwashing station
Indicators

## Slide 43
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Page 2/3
There are two possible camp layouts styles.
Their respective advantage are:
Corridor layout has less scattered facilities
16-family community has shorter distance to sanitation facilities for all users
Check distance to facilities
The ratio of people per latrine should only take into account functional latrines
Sufficient functional facilities for all users
Numbering each facility with a post code type for user to report issues help monitoring and service continuity
Check adapted latrine availability for people with reduced mobility
Indicators
Sanitation corridor
12 m minimum corridor width
minimum between dwellings
3 m
Maximum 5 dwellings per latrine
Dwellings
Family latrines
SANITATION CORRIDOR LAYOUT
16 FAMILY COMMUNITY LAYOUT

## Slide 44
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Page 3/3
Safe evacuation of faecal sludge
Check road security rules and application
Check there isn’t any spillage
Check the destination is only an approved site
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Check the treatment eliminate disease risks (e.g. cholera vibrio, parasites)
Check the faecal sludge doesn’t contain items (e.g. solid waste) that present risk to desludging and to treatment
Check the treatment outputs are used according to National Standards and international recommendations
Check final disposal site are protected against flood and rain runoff
Check surrounding aquifers are not contaminated by treatment and disposal sites (monitor bacteriological, helminths eggs and nitrate concentration)
Check if operators and stakeholders are satisfied with treatment processes and infrastructures
Indicators

## Slide 45
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Impact
Process
Impact monitoring (punctual process at key time of the implementation – FGD / survey)
Are everyone only using toilet (or commode / potty) to defecate?
Is everyone washing their hands after defecation?
Are water sources protected from faeces contamination?
Are diarrhoeal diseases morbidity reduced?
Is the level of cost recovery sufficient to sustain the operation and maintenance of the excreta disposal system?
Indicators

## Slide 46
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Indicators
Indicators
WASH outcomes
Community participation
Community satisfaction
• There is no evidence of WASH-related disease outbreaks
• Hand washing is effectively practised
• There is no evidence of open defecation
• Sanitation facilities are consistently used and users are involved in maintaining them
• Access to appropriate sanitation facilities and resources is available to all, in line with Sphere standards
• A diverse range of people selected by the community is involved in decisions on the planning, design and maintenance of sanitation infrastructure and services
• Capacity development and a timely exit/ transition plan is agreed by communities and other key stakeholders
• Formal and informal community leaders, community organizations and institutions are identified
• A stakeholder map developed with communities is used to analyse power dynamics and for programme planning
• Communities, including more marginalized groups, influence the design of feedback and complaints mechanisms
• Diverse community members are included in identifying local priorities, problems and their own solutions
• Implementation plan with roles and responsibilities of all actors is agreed and monitored
• Community members are involved in monitoring programme activities and in the feedback loop to their wider community
• Communities are supported to advocate on their behalf to Oxfam and to other stakeholders
through coordination platforms
• Marginalized groups and individuals express satisfaction with consultation and programme adaptations
• Communities report that key information is clearly communicated in appropriate languages and reaches all sections of the community using context-specific channels
• Communities report that specific gendered needs of women and men, boys and girls are taken in to account in the design and location of the facilities (access, privacy, safety, menstrual hygiene management-friendly)
• Communities report that they have the skills and support to manage WASH facilities and services
MATRIX OF INDICATORS FOR MEASURING COMMUNITY PARTICIPATION AND SATISFACTION IN RELATION TO WASH IN THE INITIAL 4 TO 6 MONTHS OF RESPONSE
Page 1/4

## Slide 47
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Indicators
Impact
GLOBAL WASH CLUSTER REPOSITORY OF INDICATORS TO MEASURE NEEDS AND RESPONSE
Code | Sub-domain | Title
AAP-1 | Feedback mechanism | Number of feedback received (including complaints) which have been acted upon
AAP-3 | Participation | Number of persons consulted (disaggregated by sex/age) before designing a program/project [alternatively: while implementing the program/project]
W 7-1 | W7 Aggravating Factors | Presence of faecal-oral diseases
W 7-4 | W7 Aggravating Factors | Density of settlement in m2 of total site area per person
W 7-5 | W7 Aggravating Factors | Nb of people on the site
W1-8 | W1.2 Hygiene Practices | Proportion of men, women, boys and girls who last defecated in a toilet (or whose faeces was last disposed of in a safe manner)
W1-9 | W1.2 Hygiene Practices | Proportion of men, women, boys and girls washing hands with water and soap or substitute after contact with faeces and before contact with food and water
W3-1 | W3.1 Environment | Presence of human faeces on the ground on and around the site
W3-2 | W3.2 Toilet Facilities | Average number of users per functioning toilet
W3-3 | W3.2 Toilet Facilities | Proportion of households with access to a functioning toilet
W3-4 | W3.2 Toilet Facilities | Proportion of toilets with functioning and convenient handwashing facilities
W3-5 | W3.2 Toilet Facilities | Proportion of toilets that are clean
W8-1 | W8 WASH Programme Design and Implementation | All groups within the affected population have equitable access to WASH facilities and services
W8-2 | W8 WASH Programme Design and Implementation | The WASH response includes effective mechanisms for representative and participatory input from all users at all phases
W8-3 | W8 WASH Programme Design and Implementation | The affected population takes responsibility for the management and maintenance of facilities as appropriate, and all groups contribute equitably
Page 2/4

## Slide 48
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Indicators
THE ACCOUNTABILITY & QUALITY ASSURANCE INITIATIVE
Page 3/4
Reference: L. Lacan & J. Brown, The accountability & quality assurance initiative – measuring what matters
VANITY vs ACTIONABLE METRICS
The AQA approach

## Slide 49
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Operation & maintenance
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Consultation
Monitoring
Excreta disposal system
Assessment
Main page
Annexes
Process
Impact
Indicators
Page 4/4
Example of contextualised module
Example of quality snapshot chart
Reference: L. Lacan & J. Brown, The accountability & quality assurance initiative – measuring what matters

## Slide 50
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Construction mode
Public toilet
Family shared toilet
Household toilet
Annexes
Excreta disposal service is required from day one of an emergency onset. The modality of implementation needs to be adapted to the targeted population and to the phase of the emergency.
1st phase / onset emergency
2nd phase / stabilisation period
Recovery / exit phase
Early recovery
Open defecation management
Trench latrine
Communal latrine
Distribution of commode and potty (children and people with disabilities
Family shared toilet
Household toilet
Inclusion of marginalised population
Sustainable system / waste to value
CLTS
Sanitation marketing
Consultation / community engagement

## Slide 51
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Construction mode
Public toilet
Family shared toilet
Household toilet
Annexes
There are a number of ways of constructing sanitation facilities:
The entire latrine can be constructed by the agency
The beneficiaries can dig their own pit & the agency provides the slabs, superstructure and technical assistance.
The beneficiaries are mobilised to construct their own latrines using locally available materials. The agency may need to provide tools and technical assistance or vouchers (conditional cash)
Using contractors & ensuring good monitoring and sign off by the agency
For contracting works, refer to Oxfam Technical Brief TBN12 – Introduction to contracting out PH engineering works and contract management and to your logistic department
In cases of large-scale emergencies when agencies have to directly install a huge number of lifesaving sanitation facilities in a short period of time, contracting out the construction work to multiple contractors is a key implementation modality. Awarding the whole work to one contractor selected via competitive bid just simply to follow the procurement rules involves accepting risks that could complicate the implementation process. Instead, distributing the work to multiple contractors will help speed up implementation and avoid risk of delay and failure in terms of quality. This requires the WASH and Logistics managers to work together.
Contracted works is a collaboration between Logistic, Finance and WASH teams and need to be well coordinated. More information can be found by Oxfam staff on the compass page One Oxfam Supply & Logistics Toolkit . Other organisations’ staff should check their organisation procedures.
Construction modalities
While contracting works has its own monitoring requirement related to contractual obligation and risk management, monitoring and sign-off also apply to all modalities albeit with less contractual constraints

## Slide 52
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Public toilet
Construction mode
Family shared toilet
Household toilet
Annexes
Whenever there is more than 20 people per latrine door
(e.g. Sphere standard for 1st phase emergency 50 people per door)
Multiple door Pit latrine
Deep Trench latrine
In the preparation phase there should be as much co-ordination as possible with the affected population concerning the siting and type of latrines. Site maps should be drawn up to aid the equal distribution of communal latrines and to plan where latrine corridors can be put. A map can be drawn up with community members to involve them in this process of siting the latrines. If a community map is used it is very important to conduct this exercise with men and women and also with a technical advisor present to ensure that a consensus is reached on this important point
Due to management and maintenance problems associated with communal facilities, communal latrines are normally seen as only a short-term measure, before family latrines can be built or only for public places such as near markets, food and health centres. It may be necessary to pay workers (per latrine completed) in the initial phase for construction of communal latrines. However, it is preferable, in order to promote ownership, care and maintenance, if community members can be motivated to build them. If community members are to build their own toilets, then it may be necessary to provide help to those who may have no one available to do this such as female headed households, disabled families and the elderly.
It may not always be necessary to construct communal latrines as the population may be rapidly mobilised to dig their own family latrines, which are always preferable if conditions allow.
In planning budgets, consider if the initial communal latrines can be reused during the transition to family shared / household toilet and include the necessary budget for their adaptation based on consultation with users.
Public Toilet

## Slide 53
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Family shared toilet
Construction mode
Public toilet
Household toilet
Annexes
Maximum 20 users per latrine door, dedicated to few families (~4) and the means to lock the door
All different modalities of construction can apply, although user participation in the construction improves user ownership of toilets
Single door structures if space allows, or double door structures
Family shared Toilet

## Slide 54
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Household toilet
Construction mode
Public toilet
Family shared toilet
Annexes
Page 1/4
Supporting families to build their own toilet through subsidies
Technical manpower
Tools
Materials
Targeting for:
Fully subsidised toilet
Partially subsidised
No subsidy
Must be discussed and agreed on with communities
Household Toilet

## Slide 55
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Household toilet
Construction mode
Public toilet
Family shared toilet
Annexes
Page 2/4
Motivating families to construct their own toilets through participatory approaches, e.g. CLTS
Triggering
Technical support for appropriate latrine design in difficult ground condition
Pre-Triggering: ensuring conditions are favourable for the CLTS approach
CLTS concentrates on the whole community rather than on individual behaviours
Reference: Plan - Handbook of Community-led Total Sanitation
Post-Triggering: Celebrating achieving ODF (Open Defecation Free) status
The facilitation phase involves a community engagement process where WASH engineers listen to users and understand enablers and barriers

## Slide 56
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Household toilet
Construction mode
Public toilet
Family shared toilet
Annexes
Page 3/4
Supporting families to build their own toilet through Market-based programming
Based on Oxfam Philippines’ program to make toilet affordable
Getting government buy in to use existing social support mechanisms to increase toilet ownership and use
Making it easy to save for a toilet or take out an affordable loan
Showing people that owning a toilet could become a reality through affordable loan and savings
Understanding the type of toilets people want to use and maintain
Reducing cost through bulk buying materials, developing local supply routes and using sales agent
Designing new, more affordable and more desirable products to suit a range of customers

## Slide 57
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Household toilet
Construction mode
Public toilet
Family shared toilet
Annexes
Page 4/4
In which situation should you consider market-based or cash-based programming?
There are artisans and small business which can easily deliver any part of the excreta disposal system (e.g., material production, construction of facilities, desludging) through capacity building or financial support
People have an income and access to market
People have access to credit or savings groups
In refugee camps, people rarely have access to income
Hiring the service of local enterprise for the upgrade or construction of latrine for IDPs / refugees families and their host
In affected communities and communities hosting IDPs / Refugees
Conditional cash grant for toilet (through vouchers) to households building their own toilet or for vulnerable families (either in host communities or camps)
Identifying micro-finance institutions and supporting access to credit
Supporting communities and artisans / enterprise in designing appropriate sanitation infrastructure
The market need to be monitored to avoid prices inflation or any other negative impact resulting from the intervention and / or from other reasons that can be beyond the control of the program
In designing think in capital investment and operational cost. The latter should be as low as possible for long term sustainability
To support loan request, think in term of return in investment (income) but also prevention in future cost / expense (reduction on health expense, less water treatment cost, reduced disaster impact, reduced water stress, etc.)
Find out more in: GWC, J. Allen & J. Brown – Market Based Programming in WASH, Technical Guidance for Humanitarian Practitioners, 2nd edition, Sept 2021

## Slide 58
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lighting
Reduced mobility
Wheelchair
Menstrual Hygiene
Reference: WaterAid (2018) - Understanding and addressing equality, non-discrimination and inclusion in water, sanitation and hygiene (WASH) work. Water Aid: London, UK
Annexes
There is no one-size-fits-all solution that can be picked up and apply to make WASH work inclusive; a range of different things need to be done, adapted to the specific context.
It’s not a linear process either; some activities can be carried out at various times in the programme cycle, and some can be run in parallel. An activity may result in unexpected outcomes, requiring you to respond in ways you had not originally anticipated, adapting your approach.
Focusing on the principles of the rights to sanitation will help guide your journey towards equality, non-discrimination and inclusion in WASH.
‘The human right to sanitation entitles everyone without discrimination to physical and affordable access to sanitation, in all spheres of life, which is safe, hygienic, secure, socially and culturally acceptable, which provides for privacy and ensures dignity.’
United Nations General Assembly / Human Rights Council

## Slide 59
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lighting
Reduced mobility
Wheelchair
Menstrual Hygiene
Annexes
Sanitation facilities are only effective if they are used, and they will only be used if the experience of using them is acceptable. This means users must feel safe and be able to see what they are doing inside the toilet. Whilst lighting may initially be viewed as a costly extra, especially in addition to the cost of a basic superstructure, its benefits justify the investment. Planning lighting in advance helps ensure that it is both efficient, effective and contributes towards greater safety, especially for women and children.
Reference: Oxfam Technical brief – Lighting for Sanitation facilities
NATURAL LIGHT INSIDE THE TOILET
Painting walls, door, floor in light color to reflect light
Window at the top of the wall or space between top of the wall and roof
Window on the roof or using material allowing light through (e.g. clear plastic sheeting)
ARTIFICIAL LIGHTING INSIDE THE TOILET
Torches and lamp
Fixed lighting
LIGHTING THE WAY
A clear, smooth path with no obstacles marked with light-coloured stones, easier to follow
Different paths to separated men’s and women’s toilets increase privacy and safety
Lantern attached to post or building, powered through battery charged by solar panel or electricity grid
If public lighting is limited, it will attract more than just insects at night. Children doing homework or men meeting to chat and drink may gather beneath it. If the only light is near a toilet, users are very visible, and this may discourage their use. Too much lighting may make going to the toilet obvious to those who would prefer the cover of darkness. Consultation with a variety of users and ongoing monitoring is the only way to fully understand what is working and what needs further adaptation
Phosphorescent sheeting experimented by French Red Cross in Madagascar
Lighting

## Slide 60
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Reduced mobility
Lighting
Wheelchair
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 1/5
Siting
Path to toilet
Entrance
No more than 15 m from household (with member with reduced mobility)
Entrances must be: a) wide enough (wheelchair width + 20cm), and b) level enough (minimal or no difference between outside and inside)
Suitable for: everyone, especially users with a visual impairment and with physical impairments, including wheelchair users.
Guide string from house to latrine and bath shelter
Clear, level path, lined with rocks
Landmark posts made from local materials
Wide and level entrance to allow wheelchair access or user with helper. Rammed earth floor.
Latrine with level concrete entrance, wide enough for a wheelchair user
Level concrete threshold with raised cement mound to reduce flooding. Mound is rounded for wheelchair access.
Reduced Mobility

## Slide 61
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Reduced mobility
Lighting
Wheelchair
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 2/5
Door
Door handles and closing mechanisms
Suitable for: users with mobility devices, a helper, or carrying a small child, or people who are overweight.
Latrine with a curtain for privacy made of light cloth
Outward-opening tin door on wooden frame. Raised platform edge acts as a door stop
Outward-opening wooden double doors with a latch on outside to keep closed
Suitable for: everyone, especially women and girls
Horizontal handrail the full width of the door on the inside. Internal bolt.
Carved wooden handle nailed to the inside of the door
Metal hook and eye on inside of door

## Slide 62
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Reduced mobility
Lighting
Wheelchair
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 3/5
Internal space
Floor finish
Think about: who will use the toilet, and how much space they will need.
Level 1: Space for users who can stand and enter using support rails, or blind users.
Level 2: Additional space for a carer, to use crutches/sticks or to park a wheelchair but not turn.
Level 3: Space for a wheelchair to enter, shut the door, and turn around inside.
Think about: the balance between hygiene and safety. Floors need to be smooth enough to be washed and swept, but not so smooth that they are slippery when wet.
Traditional round superstructure, cement seat, wooden handrail each side, curtain for privacy
Entrance corridor, with wall on left in front of latrine and a gap between corridor and toilet
Spacious toilet cubicle, with drop hole located in the corner to provide maximum usable space
Rammed earth floor without marram
Rammed earth floor made of marram (small stones) and sand; cow dung is smeared over to make it even and smooth
Cement slab, installed level with earth floor around it

## Slide 63
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Reduced mobility
Lighting
Wheelchair
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 4/5
Handrail and support
Fixed seat pan
Suitable for: People who are unstable or unable to walk, squat or stand unaided
Bricks protruding from wall for support to a weak or visually impaired person
Wooden/ bamboo support rails fixed to floor either in front or on either side of toilet (depending on user’s needs)
Metal bars (e.g. galvanised iron pipe) fixed to side wall/s of latrine
Suitable for: people who have difficulty squatting, including overweight people, pregnant women, older people and disabled people.
Twin cement-plastered brick sitting blocks
Brick seat with a cement screed
Cement bowl made with mould

## Slide 64
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Reduced mobility
Lighting
Wheelchair
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 5/5
Moveable seat
Commode seat
Suitable for: users who have difficulty squatting, including overweight people, heavily pregnant women, older people, disabled people
Low wooden or bamboo toilet stool with hole in seat, placed over toilet hole, with or without funnel as a splash guard (see lower image)
Standard varnished wooden chair with hole cut in the seat
Suitable for: people who cannot reach a latrine; small children
Painted wooden chair with ‘potty’ inserted in hole in seat. Potty is removed for emptying.
Metal commode chair with plastic inset toilet pan (bought in local market). Container is placed beneath the seat and emptied into the latrine
Oxfam Supply Centre – Code HCWOW

## Slide 65
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Wheelchair
Lighting
Reduced mobility
Menstrual Hygiene
Reference: WaterAid – Compendium of accessible WASH technologies
Annexes
Page 1/2
Wheelchair access

## Slide 66
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Wheelchair
Lighting
Reduced mobility
Menstrual Hygiene
Reference: NDA - Building for Everyone: A Universal Design Approach
Annexes
Page 2/2

## Slide 67
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Menstrual Hygiene
Lighting
Reduced mobility
Wheelchair
Annexes
Reference: Sommer, M., Schmitt, M., Clatworthy, D. (2017) – A Toolkit for integrating menstrual hygiene management (MHM) into Humanitarian Response (First Edit). New York: Columbia University, Mailman School of Public Health and International Rescue Committee
Women and girls require more privacy for sanitation than men and boys, especially when dealing with menstruation. Maintaining safety and dignity while accessing sanitation facilities remains a widespread challenge in humanitarian contexts.
Page 1/3
Menstrual Hygiene Management

## Slide 68
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Menstrual Hygiene
Lighting
Reduced mobility
Wheelchair
Annexes
Page 2/3
Reference: Sommer, M., Schmitt, M., Clatworthy, D. (2017) – A Toolkit for integrating menstrual hygiene management (MHM) into Humanitarian Response (First Edit). New York: Columbia University, Mailman School of Public Health and International Rescue Committee

## Slide 69
Adaptation for easier access
Modalities of implementation
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Menstrual Hygiene
Lighting
Reduced mobility
Wheelchair
Annexes
Page 3/3
MHM-RELATED NFI CONSIDERATIONS TO SUPPORT THE WASHING AND DRYING OF MATERIALS:
• Provision of MHM-designated buckets or basins with lids (as girls and women will not want to use the same buckets for cooking and other laundry activities). It can also be used for soaking and storage when not in use.
• Additional laundry soap for girls and women to wash menstrual materials
• A clothesline and clips to ensure girls and women can dry materials separately.
• In some contexts, women may want a piece of cloth to privately cover these materials while drying.
Reference: Sommer, M., Schmitt, M., Clatworthy, D. (2017) – A Toolkit for integrating menstrual hygiene management (MHM) into Humanitarian Response (First Edit). New York: Columbia University, Mailman School of Public Health and International Rescue Committee

## Slide 70
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Signage
Lock
Annexes
Handwashing
Reference: WEDC – Latrine superstructure
A latrine superstructure is a shelter which provides privacy and protection for the user of the latrine. Superstructures can be built from a variety of materials ranging from bricks, blocks and stone to corrugated metal sheets, wattle and daub and, in emergencies, even plastic or sackcloth.
Together with the defecation hole, it is considered by many users to be the most critical component. It is essential, therefore, that the superstructure meets their requirements. For most users, issues of security, dignity and prestige take precedence over public health consideration
Floor area: too large and people in public latrines may be tempted to defecate on the floor, particularly if the squat hole has been fouled by previous users.
For wheelchair user: doorway and floor area must be large enough to allow entry and turning.
For women and girls: superstructures with washing facilities help women and girls manage menstruation.
Height of the superstructure: should accommodate a person standing upright and be high enough to prevent the space from feeling oppressive. However, if people are used to stooping on entry to buildings, a low entrance may be acceptable or even preferred.
There is no accepted minimum size for a superstructure floor, but it would normally be greater than 0.8m wide by 1.2m long, provided the access door opens outwards. If the door opens inwards, then the length must be increased by at least 0.5m
For superstructures not attached to buildings, there are two basic shapes: a simple round or rectangular space with or without a privacy wall, a barrier in front of the entrance door to give privacy to those entering or leaving the toilet and a spiral which may also be round or rectangular.
Spiral design uses more wall materials but keep the inside of the latrine dark (requirement for Ventilated Improved Latrines)
In some cultures, there may be a prohibition on facing in a particular direction when defecating. This must obviously be considered when the latrine is being positioned.
Privacy, protection, health
Size
Shape (plan view)

## Slide 71
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed and : WEDC – Latrine superstructure
Page 1/4
Signage
Material
A roof is not necessary.
It protect the user from rain and sun.
Check local custom as in some cultures people are used to defecating in the open and find it objectionable to have to go into a small building.
What is the construction style in the area (superstructure and material used)? Avoid better construction standard than local dwelling as it won’t be affordable for other families to copy and build their own latrine outside of subsidised program.
Similarly, the introduction of new materials and methods should normally be avoided in a latrine programme as this diverts attention from the real purpose of the sanitation system. It is better to use local skills and materials which local tradesmen understand how to use and, most importantly, how to maintain.
In the initial consultation, local material availability, people’s preferences & needs regarding roof, shape, size should be identified

## Slide 72
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed and : WEDC – Latrine superstructure
Page 2/4
Bamboo
Shelters can be made from larger-diameter bamboo poles forming the main frame with smaller bamboos nailed or strapped to them to form the walls. Alternatively palm leaves or bamboo matting can be used to fill in the walls of the bamboo frame.
Sawn timber
Increasingly, sawn timber is becoming an expensive and rare commodity in low-income areas, but if off-cuts are available from a sawmill, these can be used to clad a simple timber-framed structure.
Sun-dried bricks
Known as adobe, modagadol, kacha or by other local names, made from a mixture of well-puddled and tempered clay. Moulded in simple wooden formers, and allowed to dry slowly, out of direct sunlight. Can be strengthened with the addition of natural fibres such as fine grasses or coconut fibres. The superstructure is erected slowly using mud mortar, and where necessary the walls can be strengthened with the addition of fencing wire on alternate horizontal joints.
Machine-pressed blocks
This technique employs a portable steel press to compact prepared soils in order to produce regular blocks. The blocks may be stabilized with up to 8% of cement or lime depending upon the character of the soils used and the degree of exposure of the finished wall. The blocks are laid in mud mortar and can be plastered externally with mud mortar which requires attention every couple of wet seasons.
Fired bricks
Where also used for housing, these make an excellent material for latrine construction. To exert minimum pressure on the ground, a half-brick wall (112 mm thick) built in cement mortar is used with pillars at the corners. If mud is used as the mortar to reduce costs, then a one-brick wall (225 mm thick) should be constructed.
Signage
Mud and wattle
Consist of upright poles, with the bark removed, interwoven with small branches, the whole being plastered with mud.
Mud and wattle may be improved by nailing bamboo strips to straight upright poles and filling the gaps with small stones before plastering with mud.
Stone
Traditional building techniques with stones are sometimes used for latrine construction. This is normally to be avoided over direct pits as the thickness of the walls (often 450 mm or more) exerts a high load, requiring a strong pit lining for support. Stone buildings are quite acceptable, however, for offset pits.

## Slide 73
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed and : WEDC – Latrine superstructure
Page 3/4
Ferrocement
A strong cement mortar pressed into three or four layers of wire mesh forms a strong, reasonably stiff membrane known as ferrocement. This material has been used successfully for spiral superstructures but can only be used where cement costs are low, and the people are willing to accept a new technology along with their new latrines.
Roofing
Materials such as thatch, palm leaves, clay tiles, fibre-cement tiles, wood shingles, corrugated iron, corrugated aluminium, asbestos cement, ferrocement and precast concrete can all be used for roofing the latrine superstructure. An important point to note is that the roof must be adequately tied into the wall structure and the walls must be strong enough to resist the uplift of high winds. Some materials, for example, galvanized corrugated iron, lead to greatly increased temperatures inside the latrine which may increase odour and make the building less pleasant to use.
Doors
Where possible it is advisable to mount the door on self-closing hinges. Doors can be made of sawn timber, from beaten tins or corrugated iron on a wooden frame, bamboo strips or anything else that is available. Simple curtains may suffice where timber is scarce. Where spiral designs is used without door it is normal for people to knock on the outside of the structure before entering to warn anybody using the latrine of their approach. However, check users’ preference.
Hinges do not have to be manufactured in steel; strips of old car tyres or leather from old shoes can equally well be used.
Important
Care must be taken to ensure the walls of a superstructure made of brick or blocks are not too heavy if the superstructure is built directly above a pit. Heavy walls can place undue pressure on the foundations, causing the pit to collapse.
Other wall materials
Plasticized materials, corrugated asbestos cement, galvanized iron and aluminium sheets are also used.
Signage
Concrete blocks
Where a more expensive standard is acceptable, or if firewood for brick firing is restricted concrete blocks can be made by hand on site or purchased from a local manufacturer. The blocks are usually 150 mm thick but to reduce materials 65-mm blocks can be made. However, greater skill is required in the laying of these blocks, and it is unlikely that a householder would be able to build without skilled assistance.
Vent pipe (for VIP, Ventilated Improved Latrine)
Minimum 150mm (smooth surface) or 200-250mm (rough surface) internal diameter pipe with a fine mesh at the top. Pipe made with unplasticized PVC, bricks, blocks, hollowed-out bamboo, ant-hill soil, cement rendered reeds or bamboo, and cement-rendered hessian. Flyscreen made with aluminium, stainless-steel or PVC-coated glass-fibre mesh, size of 1.2-1.5 mm. For the flytrap to be effective, the pipe needs to be directly under sunlight for heating and inside the cubicle should be dark, and the drop hole not covered for air circulation
For a VIP to be effective all the conditions need to be respected. Any of the following happening rendered the extra cost of building a VIP latrine useless:
Not dark inside the cubicle
A cap on the drop hole
The absence of mesh on top of the pipe
Wrong pipe diameter (e.g. 4” or smaller)
Shading of the pipe (e.g. installed inside the cubicle where it can represent a source of cross-contamination by hand contact, or shaded by another building)

## Slide 74
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Page 4/4
Emergency kits for latrine superstructure, suitable for first 3-4 months, camp settings
Latrine superstructure – Code LST
Latrine kit, raised, with two cubicles – Code LRLT
Sheeting, Reinforced Woven Plastic, Tarpaulin pieces – code SPT
Sheeting, Reinforced Woven Plastic, Roll – Code SPE
Reference: IFRC, Oxfam – A guide to the specification and use of plastic sheeting in humanitarian relief
Signage

## Slide 75
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Wind proofing
Material
Environment
Privacy screen
Lock
Annexes
Handwashing
Page 1/3
Reference: Habitat for Humanity - Hurricane resistant wooden houses - safer building and retrofitting guidelines
Strong foundation to anchor the structure
Foundation
Walls
Signage
Wind proofing
During the consultation step verify if there are specific risks for building in relation to strong winds and if there is a dominant wind direction

## Slide 76
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Wind proofing
Material
Environment
Privacy screen
Lock
Annexes
Handwashing
Page 2/3
Reference: Habitat for Humanity - Hurricane resistant wooden houses - safer building and retrofitting guidelines
Roof
Tie bottom up
Signage

## Slide 77
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Wind proofing
Material
Environment
Privacy screen
Lock
Annexes
Handwashing
Page 3/3
Self-closing door to avoid swinging with the wind
Spring or elastic band installed at the top.
Weight hanging on a rope fixed to the door frame
Doors
Magnet
When the door is pushed back the magnet ensure the door stay closed
Signage
However, be ready to replace / repair regularly.

## Slide 78
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Environment
Material
Wind proofing
Privacy screen
Lock
Annexes
Handwashing
Oxfam Ethical and Environmental purchasing policy
Environmental Standards
Oxfam is committed to reduce its reliance on finite/scarce resources and to minimise the environmental impact of its operations including its supply chain and will work to achieve the standards listed in this section.
Climate change:
Monitor and actively seek to reduce the Greenhouse Gas (GHG) emissions associated with its operations and:
  •Set absolute GHG reduction targets for operations in industrialised countries or Economies in Transition, such as those identified in Annex I of the United Nations Framework Convention on Climate Change below
  •Set and report on targets for improved efficiency in countries where Oxfam runs programmes, such as those that may be regarded as non-Annex I countries under the UNFCCC
Waste:
  •Reduce waste to landfill.
  •Monitor operations, including procurement, to ensure waste minimisation and high product and process efficiency.
  •Effective controls of waste in respect of ground, air, and water pollution are adopted.
Materials:
  •Reuse, recycling and the use of recycled and recyclable materials are strongly encouraged.
  •Avoid where practicable reliance on materials that are heavily dependent on finite resources.
Packaging:
  •Actively avoid undue and unnecessary packaging wherever practicable and use recycled and recyclable materials wherever appropriate.
Wood and forest products:
  •Ensure that all forest products purchased are as a minimum legal in origin and provide evidence of due diligence to ensure this if requested by Oxfam
  •Suppliers of paper products sourced from Oxfam affiliate home country offices and retail products carrying the Oxfam Brand must source forest products from recycled sources or well managed forests which have been certified to a credible standard. Exceptions will be made for products which are Fairtrade marked or produced by members of the World Fair Trade Organisation as appropriate. Oxfam views the Forestry Stewardship Council (FSC) as the most credible certification for the sustainable sourcing of wood and forest products.
  •Suppliers must never knowingly become involved in, collude with or purchase timber from illegal logging operations.
Conservation of biodiversity:
  •Seek to minimise the impact of operations on fauna, flora and land to ensure the conservation of biodiversity and habitats.
Water:
  •Develop a better understanding of its impact on water use and develop management processes where appropriate
Signage
Environment considerations
Page 1/2

## Slide 79
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Environment
Material
Wind proofing
Privacy screen
Lock
Annexes
Handwashing
Signage
Page 1/2
Step up our response to growing humanitarian needs and help people adapt to the impacts of the climate and environmental crises View guidance for commitment 1
Maximize the environmental sustainability of our work and rapidly reduce our greenhouse gas emissions View guidance for commitment 2
Embrace the leadership of local actors and communities View guidance for commitment 3
Increase our capacity to understand climate and environmental risks and develop evidence-based solutions View guidance for commitment 4
Work collaboratively across the humanitarian sector and beyond to strengthen climate and environmental action View guidance for commitment 5
Use our influence to mobilise urgent and more ambitious climate action and environmental protection View guidance for commitment 6
Develop targets and measure our progress as we implement our commitments
Oxfam International has signed the Climate and Environment Charter developed by ICRC / IFRC, committing to:
Ensure Community Engagement is mainstreamed throughout the process of developing and implementing an excreta disposal system
Include circular economy, environment protection and water security considerations into design
Integrate Environmental Impact Assessment in the process of developing an excreta disposal system
Listen, feedback, identify and share local solutions adapted to local context and climate change impact
Ensure construction with local materials (even if build by the users) doesn’t affect biodiversity and local ecosystems
Prefer solutions which minimize greenhouse gas emission (e.g., use recycled material, avoid charcoal burnt bricks, reduce methane emission by capturing and reusing as energy source, etc.)

## Slide 80
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Privacy screen
Material
Wind proofing
Environment
Lock
Annexes
Handwashing
Signage
For cultural and other reasons it can be important especially for women and girls not to be seen entering a toilet. In such situation a privacy screen can be added in front of latrine doors.
Cross bracing at corners
Bracing at least every 5 posts and should connect at 2/3 height of post
Reference: IFRC, Oxfam – A guide to the specification and use of plastic sheeting in humanitarian relief
Complete enclosed space, combining shower, latrines, handwashing stand, laundry station and drying clothes lines for menstrual hygiene management
For more on plastic sheeting quality and privacy issues See video Spotlight on privacy
Privacy screen

## Slide 81
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Signage
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
While in many countries men are traditionally represented with trousers and women with skirt, don’t assume it applies everywhere…
e.g. In Pakistan both women and men wear trousers under a tunic
Signage need to consider literacy level and local custom representation for men and women
e.g. Touareg men
Consult with users the best way to represent women and men latrines
Various signages found on internet
Oxfam Supply Centre – Code HMFLS
Signage

## Slide 82
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lock
Material
Wind proofing
Environment
Privacy screen
Annexes
Handwashing
Signage
An internal lock is an important part of ensuring privacy and safety while using latrine
The most common internal locks used, both bolt and hook type of lock failed when wood door and frame change shape over time and use.
Piece of wood to reinforce the frame on the outside of the door
String passed through a hole drilled through the door frame and piece of wood. Knotted on the outside
Piece of wood to reinforce inside wall of latrine with two nails sticking out
String wrap around the nails several time to tight the door closed
Bolt lock
Hook lock
String lock
Lock
Video Spotlight on safety

## Slide 83
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Signage
Reference: Oxfam – Handwashing stations Technical Briefing Note and the following for further reading The Sanitation Learning Hub – Handwashing compendium for Low Resource Settings
Page 1/3
Handwashing is a critical practice that is promoted to protect public health, especially during outbreaks of infectious diseases such as COVID-19. Handwashing stations are used both in emergencies and in other contexts to provide locations for people to wash hands with soap. In refugee camps and internal displacement centres, units for handwashing should be installed both at households and next to latrines and in communal areas, such as in markets, schools, and health centres. The criteria for a good handwashing station include:
Principle Considerations
Cost
Maintenance required
Ability to limit hand contact by users with a tap interface (preferably with no touch or one touch action)
Accessibility, including for children, elderly and people with disabilities
Design that promotes usage through aesthetics, behavioural nudges, and ease of use
Robustness of design that can withstand misuse or vandalism and prevent theft
Additional Considerations
Ability to drain effectively without creating stagnant greywater
Availability and ease of assembly
Packability and ease of transport
Ability to conserve water
Handwashing stations can either be procured ready-made or they may be assembled locally.
Some of the units presented are completed products that have undergone years of research and development and thorough testing with end users.
Other options present design ideas for handwashing stations that can be constructed locally.
These design concepts require further adjustment to ensure they are reliable options for handwashing, especially when installed for communal use. Such handwashing stations should be tested not only for technical performance but for user satisfaction, correct use, and degree to which they are successful in promoting handwashing behaviour.
Handwashing

## Slide 84
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Signage
Page 2/3
Reference: Oxfam – Handwashing stations Technical Briefing Note
Completed Products
1. Oxfam Handwashing Station
2. Oxfam Handy Wash Tap
3. Jengu (by ARUP, BRC, and LSHTM)

## Slide 85
Latrine superstructure
Modalities of implementation
Adaptation for easier access
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Wind proofing
Environment
Privacy screen
Lock
Annexes
Handwashing
Signage
Page 3/3
Reference: Oxfam – Handwashing stations Technical Briefing Note
Ideas for Local Assembly
4. Twin Foot Pedal Design (by WaterAid Nepal)
5. Single Foot Pedal Design
6. Long Handled Taps
Other Options for Households
7. Happy Tap
8. SpaTap
9. Oxfam Bucket
10. Tippy Tap
11. Soapy Water Bottle

## Slide 86
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Requirement
Material
Cleaning
Sitting
Waterproofing
Top face in compression
Bottom face in tension
No flexion of the slab
Annexes
Tension and compression forces in a slab
Section slab - direct drop toilet.
Section slab - offset pit
User weight
A concrete slab will stay rigid and crack where tension is the highest unless rebars are used or if the slab has a dome shape.
A plastic slab will bounce under the weight of the user, affecting users’ trust and potentially scaring children
Without lining consolidated soil capacity to withstand the weight may erode with time and water
Fractures
How much water is available for flushing? Consult with users to understand how easy or complicate is their access to water. Include an analysis of drought impact

## Slide 87
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Requirement
Material
Waterproofing
Cleaning
Sitting
Annexes
A latrine slab serves two main purposes, as a support and as a seal. It must support the weight of the person using the latrine and, possibly, the weight of the superstructure. It also seals the pit, except for the squat hole and, where required, the vent pipe hole. This facilitates control of flies and smells and reduces the likelihood of rodents and surface water entering the pit. Where the slab has been made in sections (for ease of placing and emptying) or has a removable cover, the joints should be sealed with a weak mortar such as a lime or mud mortar.
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed and WEDC – Latrine slabs: construction material
Seal. Gaps between slab and lining / pit walls sealed with soil
Slab slope. water should be directed toward the hole and away from the sides (in case of UDDT the slope should channel water toward a soakaway pit)
Durability. If the slab is going to last and not collapse suddenly, it needs to be resistant to rot and termite attack. It should also withstand repeated washing.
Cleanliness. The slab needs to be suitable for cleaning. Rough wood or rough concrete quickly becomes dirty and difficult to clean.
Surface texture. A smooth slab may be easy to clean, but if it is too smooth, then it may be slippery when wet. The inner surface of a pour-flush pan needs to be very smooth, so the faeces can be easily washed away.
Colour. To see if the slab is clean and to check for spiders, snakes or other creatures, users may prefer particular colours. Cultural and religious affiliations may influence such preferences too.
Water resistance. Urine, water for anal and menstrual cleansing and water for washing the slab will make the slab wet, so it needs to be able to withstand this and allow excess water to drain away, normally into the vault.
Strength. The slab needs to be strong enough to support the weight of the user, and perhaps someone to assist them. It needs to look strong to give people the confidence to use it.
Reuse. Once the pit is full, the slab may have to be moved, either to gain access to the vault so it can be emptied or moved to a new site.
Requirement
Pre-test your slab when consulting users

## Slide 88
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Requirement
Waterproofing
Cleaning
Sitting
Annexes
Page 1/3
Unreinforced concrete
Non-supporting slab
Self- supporting slab
Dome
SanPlat
Reinforced concrete
Slab thickness (mm) | Steel bar diameter (mm) | Spacing of steel bars (mm) for minimum slab span of |  |  |  | 
 |  | 1 m | 1.25 m | 1.5 m | 1.75 m | 2 m
65 | 6 | 150 | 150 | 125 | 75 | 50
 | 8 | 250 | 250 | 200 | 150 | 125
80 | 6 | 150 | 150 | 150 | 125 | 75
 | 8 | 250 | 250 | 250 | 200 | 150
Plastic
Latrine Slab, Plastic Self Supporting – Code LOPN
1.2m long x 0.8m wide x 35mm thick
Squatting plate,plastic,80x60cm
Material

## Slide 89
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Requirement
Waterproofing
Cleaning
Sitting
Annexes
Page 2/3
Wood
Self- supporting slab
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Durable timbers such as the heartwood of some tropical hardwoods are normally too expensive for use in latrines but, where available, may be expected to last satisfactorily for several years.
A thick layer of earth or mud is often spread over the poles or branches to bind them together and create a smooth surface (Fig. 7.22). In many places, people are skilled at making mud floors which are almost as hard as cement and quite smooth. They need not be rough or unsanitary. There are various methods of improving the mud with local materials, such as mixing the soil with a liquor obtained by soaking animal dung overnight. In some areas the mud is mixed with charcoal or other small aggregate, or with cow dung and then smeared with ashes. Alternatively, the mud from ant-hills has been found to make a hard, practically waterproof surface (Denyer, 1978).
The life of a rough timber slab can be extended by using a mixture of soil and cement to plaster and protect the wood. Alternatively, a thin cement mortar screed can be laid over the surface of the earth to protect against hookworm and to improve hygiene. However, it is usually more cost-effective to use the cement to provide a permanent concrete slab which can be transferred to a new pit when the first is filled. Where more than half a bag of cement is needed to stabilize the earth, a concrete slab is likely to be a cheaper alternative.
In an area where timber is abundant, hewn or sawn logs supporting a platform of wooden planks make a floor that is preferable to the mud and pole version (Fig. 7.23). The surface can be kept clean, and signs of imminent collapse are normally apparent to the adult user. The durability of timbers may be improved by some form of treatment.
The cost and environment impact of the wood treatment options need to be examined

## Slide 90
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Material
Requirement
Waterproofing
Cleaning
Sitting
Annexes
Page 3/3
Footrests and squat holes
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Avoid large and wide hole sizes if small children will use the latrine
Water seals and pans
Can be made in ceramic, concrete, plastic, etc.
Its weight need to be considered into the design of the slab
Verify how easy it is to flush the pan (how many litres are required) considering users’ access to water

## Slide 91
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Waterproofing
Requirement
Material
Cleaning
Sitting
Annexes
Seal with soil the spaces between slab and pit walls
Seal the side of the latrine walls by covering the extra length of plastic sheeting with soil
Shape a drainage channel under the overhanging roof edge to collect and evacuate rain dripping from the roof
Soil shaped into a bank to divert rain and water runoff from the latrine pit
Water proofing
When locating sanitation infrastructures pay attention to topography to ensure water runoff path does not cross where latrines are located.
You can get information from local population on drainage pattern during the consultation process.

## Slide 92
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Cleaning
Requirement
Material
Waterproofing
Sitting
Annexes
Latrine cleaning kit adapted to context
A washable slab (plastic, ceramic, concrete, wood covered with plastic sheeting)
Designated people for daily cleaning duty
Users
WASH committee
Public toilet
Family and family shared toilet
Cleaning
If payment of latrine attendants is considered it should be restricted to public toilets, with a fee contribution scheme from users for sustainability or with a clear transition plan and communication toward users taking over (e.g. when transitioning to family shared or family latrines)

## Slide 93
Slab
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Sitting
Requirement
Material
Waterproofing
Cleaning
Annexes
In many parts of the world, people prefer to sit to defecate. To make a latrine seat, a support or pedestal is built or mounted on top of the slab. The seat level should be at a position that is comfortable for the majority of the users (Fig. 7.26); this is normally about 350 mm above the top of the slab.
The seat support can be made on site from brick, concrete, mud block or timber and should be designed to minimize the load on the slab. A heavy type of construction adds weight to the slab which then requires more expensive reinforcement to carry the load. Commercially available or project-manufactured pedestals made of ceramic, glass reinforced plastic (GRP), PVC or ferrocement can also be used where people can afford them.
Reference: WEDC repository
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Wood seats
Reference: GTZ – Technology Review of UDDTs
Special seats
For sitting, wood can be warmer and smoother than concrete but perhaps more difficult to keep clean. Wooden seats are simpler to make locally. Plastic can be easy to clean but, if flexible, can be disconcerting to use. Concrete blocks are strong but not very comfortable.
Reference WEDC – Latrine slabs: construction material
Sitting

## Slide 94
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Soil considerations
Pre-treatment
Lining options
Reference: WEDC – Latrine pit design booklet
The need for a pit lining depends upon the type of latrine under construction and the condition of the soil, as well as desludging service
Annexes
Grey water
Circular shapes are stronger than rectangular !

## Slide 95
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Soil considerations
Pre-treatment
Lining options
Annexes
Ground conditions
Ground conditions affect the selection and design of sanitation systems, and the following five factors should be taken into consideration:
Bearing capacity of the soil
All structures require foundations, and some soils are suitable only for lightweight materials because of their poor load-carrying capacity - marshy and peaty soils are obvious examples.
Self-supporting properties of the pits
Many soils may appear to be self-supporting when first excavated, particularly cohesive soils, such as clays and silts, and naturally bonded soils, such as laterites and soft rock. These self-supporting properties may well be lost over time owing to changes in the moisture content or decomposition of the bonding agent through contact with air and/or moisture. It is almost impossible to predict when these changes are likely to occur or even if they will occur at all. It is therefore safer to line the pit. The lining should permit liquid to percolate into the surrounding soil.
Depth of excavation
Loose ground, hard rock or groundwater near to the surface limit the depth of excavation possible using simple hand tools. Large rocks may be broken if a fire is lit around them and then cold water poured on the hot rock. Excavation below the water table and in loose ground is possible by "caissoning", but it is expensive and not usually suitable for use by householders building their own latrines.
Page 1/2
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Pore clogging
Soil pores eventually become clogged by effluent from pits or drainage trenches. This may reduce or even stop infiltration through the soil. Clogging may be caused by:
- blockage of pores by solids filtered from the liquid;
- growth of microorganisms and their wastes;
- swelling of clay minerals; and
- precipitation of insoluble salts.
Grey water
Soil considerations
Local knowledge can help determine such risks
Caisson waterproofing must be ensured when the water table is less than 1.5m. In addition Archimedes law may apply if the caisson is reached by water with a thrust force moving the caisson up and damaging it. All in all not a good idea…

## Slide 96
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Soil considerations
Pre-treatment
Lining options
Annexes
Determining infiltration rates
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Page 2/2
Infiltration rate
The soil type affects the rate at which liquid infiltrates from pits and drainage trenches. Clays that expand when wet may become impermeable. Other soils such as silts and fine sands may be permeable to clean water but become blocked when transmitting effluent containing suspended and dissolved solids.
The rate of infiltration also depends on the level of the groundwater table relative to the liquid in the pit or trench. In the unsaturated zone, the flow of liquid is induced by gravity and cohesive and adhesive forces set up in the soil. Seasonal variation may produce a change in the amount of air and water in the soil pores and this will affect the flow rate. Conditions at the end of the wet season should normally be used for design purposes as this is usually the time when the groundwater level is at its highest. In the saturated zone all pores are filled with water and drainage depends on the size of the pores and the difference in level between the liquid in the pit or trench and the surrounding groundwater.
Soil porosity also affects infiltration. Soils with large pores, such as sand and gravel, and rocks such as some sandstones and those containing fissures, drain easily. Silt and clay soils, however, have very small pores and tend to retain water. Soils containing organic materials also tend to retain water, but the roots of plants and trees break up the soil, producing holes through which liquids can drain quickly.
The rate of groundwater flow in unsaturated soils is a complex function of the size, shape and distribution of the pores and fissures, the soil chemistry and the presence of air. The speed of flow is normally less than 0.3 m per day except in fissured rocks and coarse gravels, where the speed may be more than 5.0 m per day, with increased likelihood of groundwater pollution.
In fissured rocks conditions, it’s advised to add sand at the bottom to create a biological filtration layer and reduce pollution (minimum thickness 0.5m)
Grey water

## Slide 97
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pre-treatment
Soil considerations
Lining options
Annexes
The decomposition is mainly carried out by bacteria although fungi and other organisms may assist. The bacterial activity may be either aerobic, i.e., taking place in the presence of air or free oxygen (for example, following defecation and urination on to the ground), or anaerobic, i.e., in an environment containing no air or free oxygen (for example, in a septic tank or at the bottom of a pit). In some situations, both aerobic and anaerobic conditions may apply in turn. When all available oxygen has been used by aerobic bacteria, facultative bacteria capable of either aerobic or anaerobic activity take over, and finally anaerobic organisms commence activity.
As soon as excreta are deposited, they start to decompose, eventually becoming a stable material with no unpleasant smell and containing valuable plant nutrients. During decomposition the following processes take place.
• Complex organic compounds, such as proteins and urea, are broken down into simpler and more stable forms.
• Gases such as ammonia, methane, carbon dioxide and nitrogen are produced and released into the atmosphere.
• Soluble material is produced which may leach into the underlying or surrounding soil or be washed away by flushing water or groundwater.
• Pathogens are destroyed because they are unable to survive in the environment of the decomposing material.
Pathogens may be destroyed because the temperature and moisture content of the decomposing material create hostile conditions. For example, during composting of a mixture of faeces and vegetable waste under fully aerobic conditions, the temperature may rise to 70°C, which is too hot for the survival of intestinal organisms. Pathogens may also be attacked by predatory bacteria and protozoa, or may lose a contest for limited nutrients.
O2
O2
Reference: Wikipedia
Page 1/3
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Grey water
Pre-treatment

## Slide 98
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pre-treatment
Soil considerations
Lining options
Annexes
Where possible and if the numbers are below 20,000 on site treatment, septic tanks, biogas or Anaerobic Baffled Reactor (ABR) with leachfields, Urine Diversion Dehydration Toilet (UDDT), or Tiger Worm toilets should be used to decrease desludging, transportation and disposal costs. However, all of these technologies need desludging at some point and that needs to be factored into the design and service provision. Compared the estimated desludging times for Communal pit latrine (trench 3x4x1m) which is 3 months with on-site treatment in emergency contexts
Page 2/3
Safe Treatment
Anaerobic Treatment
Septic Tanks – desludged every 2 years
ABR – desludged every 6 years
Biogas – Desludged every 6 years
Tiger Worm Toilets – desludged every 5 years
Double vault UDDT – desludged every 1 year
Dehydration
Vermi-composting
Reference “Compendium of sanitation technologies in Emergencies”
Grey water
This is a design parameter. Any duration increase before desludging and the risk to clog the percolation filter with sludge increase as well as cost for repair and maintenance

## Slide 99
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pre-treatment
Soil considerations
Lining options
Annexes
Soakaway pit (e.g. in association with UDDT for managing cleaning water) for small effluent volume
Reference: GRET – Memento de l’assainissement and “Compendium of sanitation technologies in Emergencies”
Simplified sewerage to connect several latrines to one pre-treatment unit such as septic tank, ABR or biogas digestor:
Pipe diameter 100 to 200 mm
Minimum slope 1% for self-cleansing and water consumption at least 50l/p/d (or minimum 0.5% slope with a minimum water consumption of 60 l/p/d)
Inspection box at each household with grease trap if kitchen grey water is collected
Simple inspection chamber diameter 400 to 600 mm (at junction, direction change, slope change, every 50 m for inspection and cleaning / unblocking pipe)
Depth minimum 30 cm (no pressure from vehicle traffic) or 60 cm under vehicle access road
Outline as straight and short as possible
Attention need to be paid to pipe and inspection chambers’ foundation to avoid movement and future counter slopes. A trained O&M team should be in place to deal with blockage and maintenance.
Septic tank, Biogas digester, ABRs and UDDT must be connected to infiltration system to dispose of effluent
Vertical percolation
Horizontal percolation
Leach field (e.g. in association septic tank) for larger effluent volume.
Sewerage pipes
Page 3/3
Grey water
During the consultation process, be attentive to potential co-benefit, such as urban forestry development, aquifer recharge
Successful operation requires clearly defined responsibilities between service provider and users

## Slide 100
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lining options
Soil considerations
Pre-treatment
Annexes
Reference: WEDC – Latrine pit excavation and linings
Page 1/3
Lining is needed when the soil is unstable or if it will become unstable due to water seeping up / in during rainy season or when desludging is required as the mechanical vacuum process will cause the wall to collapse
Foundations
Nearly all linings need a foundation to prevent the lining sinking into the
ground below. In firm soils a simple pad foundation about three times the width of the linings is sufficient (see Figure 7a). The foundation is usually made of the same material as the lining.
In soft ground a thicker foundation may be needed. Cover the base with a 10 to 15cm layer of compacted mixed stone and construct the foundation on that (see Figure 7b).
When only partially lining the pit, leave a step in the pit wall on which to build the foundation (see Figure 7c).
Grey water
Lining options

## Slide 101
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lining options
Soil considerations
Pre-treatment
Annexes
Page 2/3
Fig-1- Simple Pit Lining with Sandbags
Fig-2- Communal Trench Pit Lining with Bricks
Sand bags are cut and stitched in oblong shape.
Be careful, over time the top sand bags will tear from the weight and pressure exercised by the slab
Grey water

## Slide 102
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Lining options
Soil considerations
Pre-treatment
Grey water
Annexes
Page 3/3
Plastic lining
Bamboo cage lining.
Overtime the bamboo will deteriorate but should last 1 to 2 years (check local knowledge)

## Slide 103
Storage / pre-treatment pit
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Desludging
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Grey water
Soil considerations
Pre-treatment
Lining options
Grey water (because of its colour and also called sullage) consists of the liquid wastes from domestic activities such as bathing, laundry, food preparation etc. but EXCLUDING excreta related liquids, sometimes known as black water.
Risks for latrine created by grey water
Filling of latrine pits
Pit wall erosion and potential collapse
Obstruction of access paths and walkways;
Can be treated with black water and excreta, depending on the type of pre-treatment (septic tank) and treatment options (reed bed)
Annexes
Other risks created by grey water
Breeding sites for water related insect vectors
Soil erosion around temporary shelters
Filling of solid waste pits
Pollution of surface and groundwater
Reduced moral from living in a contaminated environment
The most common sources in emergency settings are:
Water taps;
Kitchens/feeding centres;
Laundries;
Bathing areas; and
Health care centres.
Typical grey water contamination from various sources | 
Source | Contamination
Kitchens | Cooked and uncooked animal and vegetable food waste, oils and fats, soap, silt and grit
Laundry | Laundry soap, silt and grit, oil, faeces, blood, urine
Bathing | Bathing soap, faeces, silt and grit, blood, urine
Health care centres | All of the above depending on the type of facility
Note: The faeces, blood and urine in laundry and bathing sullage is usually very low but can be significant from health care centres. | 
Typical grey water volumes from public institutions (Based on [2]) | 
Institution | Sullage volume
Field hospital | 40 - 60 litres/patient/day
Hospital with operating theatres | 100 litres/intervention
Out-patient clinics | 5 litre/patient/day
Cholera treatment centre | 50 litres/patient/day 10 litres/carer per day
Viral haemorrhagic fever centre | 300–400 litres/patient/day
Feeding Centre | 25 litres/person/day 10 litres/carer/day
Public bathing area – piped water provided | 100 litres/user*
– no piped water provided | 20 litres/user
Public laundry area – piped water provide | 100 litres/user*
– no piped water provided | 20 litres
Public water points | 5 – 20 litres/user*
Note: * These numbers vary widely dependent on the quality of the control mechanism on the pipe outlet and the management of the facility. | 
Grey water treatment options:
Gross solids removal
Grease traps
Settlement tanks
Reed beds
Grey water disposal technology options:
Infiltration
Evapotranspiration (ponds or beds)
Irrigation
Surface water diffusion
Reuse
Reference: R. Reed – Engineering in Emergencies – Sullage disposal
Grey water

## Slide 104
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Manual
Mechanical
Safe handling
Lining options
Annexes
Is there a desludging hole or should the defecation hole be used?
How bulky is the pumping system, and how near / far from the pit can it be located?
What are the investment cost and operation & maintenance cost of the desludging system? Is it affordable in the short / medium / long term?
When choosing a desludging system, pay attention to accessibility and manoeuvrability.
How thick is the sludge. Will water be needed to dilute before pumping out?
Can the system be locally manufactured or need to be imported?
How easy is it to use?
Is the desludging system combined with a tank for safe transport or should you purchase separately a safe transportable container?

## Slide 105
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Manual
Mechanical
Safe handling
Annexes
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Oxfam Supply Centre – Code LDP
Sludge Gulper IV
Diaphragm handpump
Page 1/2
Nibbler
Low cost, can be build locally
The Gulper 4 is a manual desludging pump for emptying toilet pits and septic tanks. It is an upgraded version of the previous Gulper pump, offering an increased pumping head of approximately 3 m and a delivery head of approximately 3 m. The pump uses flexible piping that allows for a closed system to pump directly to the back of a truck and reduces spillage. The pump has been fabricated with UK-based company BuildWorks and is currently being replicated in with local fabricators in Uganda, Malawi, Rwanda and Honduras. The engineering drawings for this pump are open-source and available from Water For People.
Others
Consist of a rigid, disc shaped body clamped to a flexible rubber membrane called a diaphragm. An airtight seal between the diaphragm and the disc forms a cavity. To operate the pump, the diaphragm is alternately pushed and pulled causing it to deform into concave and convex shapes in the same way a rubber plunger is used to unblock a toilet.
Collect medium viscosity sludge using a continuous roller chain loop enclosed in a PVC pipe.
Due to limited success during trials, development of the nibbler was suspended.
Human-powered vacuum system for the collection and short-distance transport of sludge called the Manual Pit Emptying Technology (MAPET). Due to issues with spare parts and high capital cost this technology was discontinued.
Manual desludging
Continuous chain device [Sugden, 2008]
Beaumont manual pump: a basic piston pump designed to intervene in small space, easy to repair, the SP10 - Human Powered Sludge Pump is still under development with the 4th iteration.

## Slide 106
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Manual
Mechanical
Safe handling
Annexes
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Page 2/2
The gulper IV version has a 3m pumping head, capital cost from 200 USD (local production) - 1,400 USD (UK manufacturer)
The PVC riser pipe has been replaced by a flexible pipe not prone to cracking

## Slide 107
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Mechanical
Manual
Safe handling
Annexes
Diaphragm Sludge pump
Oxfam Supply Centre – Code LDD3
The performance of a desludging pump will always be limited by two factors that are common in latrines: 1) The fluid being too thick or heavy to flow 2) Debris in the sludge blocking the inlet
Oxfam Supply Centre – Code WSDP
Trash pump
Suitable for pumping sludge with high liquid content with solids up to 30mm in diameter
Motorised pit screw auger
Page 1/2
Some of the challenges faced by the motorised PSAs include (Still and O’Riordan, 2012; Still and Foxon, 2012):
• complicated emptying process due to the fixed length and rigidity of the auger and riser pipe;
• unsuitability for use with dry sludge and large amounts of non-biodegradable waste;
• difficulties with cleaning after use; and
• difficulties manoeuvring due to weight and size.
Conventional vacuum truck
Gobbler
Vacutug
Using the same operating principles as the Nibbler, the Gobbler is powered using an electric motor. The motor turns a double chain drive that rotates a heavier gauge chain that of the Nibbler. However due to significant challenge it was not further developed
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Mechanical desludging
Photo: UN-Habitat

## Slide 108
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Mechanical
Manual
Safe handling
Annexes
Page 2/2
Reference: Feacal sludge management – Systems approach for Implementation and Operation
During the consultation process ensure you understand users’ capacity of payment compared to the cost of desludging one pit with the technical choices available.
What volume of sludge can households or group of households afford to desludge? Match latrine pit size to what households can afford.

## Slide 109
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Safe handling
Manual
Mechanical
Annexes
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Page 1/3
A desludging service will include the following tasks:
Interact with customers prior to removing Faecal Sludge (FS) to arrange logistics and inform them of procedures;
Locate onsite sanitation systems that are to have sludge removed;
Determine the accessibility of the system once it is located;
Open the system to facilitate the process;
Collect the FS;
Evaluate the condition of the system post-collection;
Close and secure the system once the FS removal has been completed;
Clean up after the process is completed; and
Perform the final inspection and report any issues with the system to the customers after the service is completed.
In a sustainable process where the service is paid by customers to cover costs the following task should be included:
Share the standardised fee or negotiate one, depending on the business model;
In a camp setting it is recommended to label each latrine with a unique code with a clue to the location (e.g., section, block, street, latrine number)
In an urban setting locating a septic tank may not be obvious and looking for clues such as manhole cover, sewer cleanout, depression in a yard, or using a probe may be required
Access will be dependent on the desludging system used (e.g., vacuum truck and the maximum pipe length) and the access road dimension or neighbour agreement if private land need to be crossed or used for setting up equipment.
The following questions can be used as a checklist to assist the service provider in determining if the system is accessible for emptying:
Can the system be opened to accommodate the sludge removal equipment (e.g., hose)?
Are there existing manholes over each compartment that can be opened?
Will the installation of new access ports be required? If so, is that a service that the residents have agreed to?
Will slabs, floors, or septic tank covers have to be rebuilt following emptying?
Will the pit collapse if emptied?
Ensuring the service
Safe handling of sludge

## Slide 110
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Safe handling
Manual
Mechanical
Annexes
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Page 2/3
Tools of the trade
Shovels, pry bars and probes to locate tanks and manholes;
Screwdrivers and other hand tools to open manholes and access port lids;
Long handle shovels and buckets which may be necessary to remove solids that cannot otherwise be removed;
Hooks to remove non-biodegradable solids;
Hoses for FS pumping as well as for adding water to tanks if available; and
Safety equipment including:
  Wheel chocks to prevent the vehicle from moving when parked;
  Personal protective equipment such as hardhat, face protection, eye protection, boots and gloves;
  Disinfectants, barriers, sorbents and bags for cleaning up and collecting spilled material.
Transport considerations
The aspects that need to be considered for the transportation of FS include:
The type of vehicle to be used including its road worthiness, maintenance, licenses and permits, and where it is kept when it is not in service;
The type of sludge removal equipment, including hoses, pumps, augers, and other tools of the trade;
The spill management equipment to be used including shovels, disinfectants, sorbents, and collection bags;
The skills of the operator including the training and certifications that might be required to perform the work;
Procedures that need to be followed including rules of the road and activities at the treatment plant; and
Other aspects such as the use of transfer stations, worker health and safety, and emerging technologies.
Pipe and fittings, if not maintained frequently, won’t function properly and leak

## Slide 111
Desludging
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Treatment
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Safe handling
Manual
Mechanical
Annexes
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Page 3/3
Transport equipment
Human or animal powered
Stability (to avoid spilling) and capacity to carry the weight should considered
Motorised
Up to 200 litres
Up to 1000 litres
10 to 55 m3
Transfer station
Intermediary storage between small size collection system and final treatment plant
It can be made of portable container or a fixed station offering some pre-treatment capacity such as Settling tank, drying beds, Biogas digestor, Septic tank, ABRs

## Slide 112
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen Inactivation
Annexes
Wastewater chain
Faecal sludge chain
ONSITE PRETREAMENT
Liquids
Reference: GWC – FSM TWIG – Terminology Factsheet
Wastewater is generally used to refer to the mixture collected in and transported through a sewer system, using flushing water to transport the faeces and urine. In addition to flushing water, wastewater generally also contains greywater, e.g. the water from showers and sinks
Faecal sludge is the mixture of human urine and faeces, water and solid wastes (such as toilet paper and menstrual hygiene materials) that gets collected in onsite sanitation systems and is not transported through a sewer
Most treatment options fall into 4 categories: physical, mechanical, chemical and biological treatment, and a full treatment chain generally involved a mix of them.
The aim of wastewater and Faecal sludge treatment is the reduction of volume by separating solid and liquid, the inactivation of pathogens and the reduction of Carbonate, Nitrogen and Phosphorus returning to water bodies before disposing safely of the final products. BOD (biological oxygen demand) is a proxy indicator of organic matter pollution used to measure potential risks presented by effluents to water bodies and their fauna and flora.

## Slide 113
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 1/8
Treatment options in emergency setting
While there are a wide variety of solutions for potable water transport, storage and treatment, most existing emergency kits in sanitation focus on latrines and sludge pumps. Developing faecal sludge treatment kit for emergency purpose is in its infancy.
Other types of treatment such as anaerobic filter, trickling filter will require a rigid tank. Metal sheet and liners have successfully replaced civil works in water emergency kits and a similar approach can be done for faecal sludge treatment.
It is certainly possible to redirect some of the existing potable water tank kit however be attentive on the liner type and its interaction with wastewater whose characteristics are different from potable water.
Selecting geotextile (for the role of support and eventually protection layer) and geomembrane (role of barrier) to design a liner system depend on the choice available locally, site characteristics, the function and geometry of the facility, the characteristic of the water to be stored, the condition of use and maintenance (including possible risks such as flood and environmental risks).
Welding, to seal geomembrane sheets, is sensitive to weather (humidity and temperature variation) and need to be carefully planned. Water and gas may accumulate underneath the geomembrane and exert backpressure on it. In this case water and gas drainage networks should be designed and installed under the geomembrane.
Oxfam is currently testing a flatpack septic tank kit separating liquid and solid and storing up to 6-12 months faecal sludge from about 500 people.
It is composed of a two chambers bladder tank,
Previous version of Oxfam T tank liners were made with EPDM which tend to swell in contact with hydrocarbon (organic matter) and change its characteristics. The suitability for wastewater need to be checked with the supplier. The current version has a PVC liner which require specific blend to be used for wastewater. Again, check with the supplier on the suitability of using the kit for wastewater. The degradation of the liner characteristics may take time, sufficiently for an emergency response use but it’s important to understand and integrate the expiration date into planning.
and a set of foldable prefabricated infiltration units

## Slide 114
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 2/8
Adapted pipe for sludge transfer: HDPE, minimum size 110mm
Slotted or perforated rigid pipe for percolation field and effluent drainage
Use appropriate valves to minimise clogging
Any filtering process risk clogging and system to backwash with water or a combination water and air to unblock pores and pipes need to be included into the design
Flood risks and their impact on the treatment plant should be considered when locating site and designing infrastructure. Overflow management should be planned to minimise groundwater contamination.
Site topography is a key factor for gravity flow design into the treatment process and minimise pumping needs.
Look beyond faecal sludge and wastewater treatment and consider how end products (treated effluent, biogas / biomass / compost / dry sludge / fuel briquette) can support climate change adaptation and water security
E.g., by supporting urban forests, agroforestry, crop irrigation, biodiversity & land management, water resource management, etc.
Where drying beds are considered, rain and runoff pathway should be mapped to minimise their impact on the treatment process. A roof on the drying beds may be required.
Can users’ needs for energy, agriculture, cooking fuel be served by the treatment process?
Other considerations for building a treatment system
Material-wise:
Design-wise:
On the selection of the treatment option:
The environment impact of a treatment system can have two objectives. The primary one is to reduce the pollution risks of water bodies (pathogen contamination and eutrophication). The second one can be to mitigate some human impact on environment such as deforestation, overextraction of aquifer… if the treatment type is carefully selected in consultation with concerned communities

## Slide 115
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 3/8
Reference: ARUP / Oxfam / UNHCR - Faecal Sludge Management for disaster Relief: Technology comparison study
Key indicators used to compare technologies were
Capital and operational costs (CAPEX and OPEX);
Area requirement and layout;
Speed of construction and commissioning;
Expertise required for set up and operate;
Operation and maintenance issues;
Process pinch points;
Quality of liquid and solid effluent (pathogen inactivation);
Disposal of final products (liquid and solid); and
Resilience to flooding/natural disaster.
Centralised (treating more than 20m3/ day of sludge and serving a large area) and decentralised (serving a smaller area and treating 2-5m3/day) system were studied
The refugees’ camps of Cox’s Bazar in Bangladesh with their lack of space and the long-term Rohingya crisis was the occasion to implement and test various treatment options in an emergency setting
Out of 8 technologies reviewed 2 rated best on several indicators:
1- Upflow filters (decentralised)
2- Anaerobic Baffled reactors – ABR (centralised)
Depending on your design parameters, check which technology fit best
Lime came out a good and robust treatment option but only during the immediate emergency phase due to its high OPEX.

## Slide 116
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 4/8
Reference: Faecal Sludge Management for disaster Relief: Technology comparison study

## Slide 117
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 5/8
Reference: Faecal Sludge Management for disaster Relief: Technology comparison study

## Slide 118
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 6/8
Reference: Faecal Sludge Management for disaster Relief: Technology comparison study
CAPEX
OPEX
Whole life cost (10 years)
$10,710 per m3 treated
$0.87 per m3 treated
$47,000
Variation in layout, by replacing 2 filters with settlement tanks
Upflow filters
Capacity
2 m3 per day

## Slide 119
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
ABR
Reference: Faecal Sludge Management for disaster Relief: Technology comparison study
CAPEX
OPEX
Whole life cost (10 years)
$342 per m3 treated
$0.06 per m3 treated
$21,160
Capacity
35 m3 per day
Page 7/8

## Slide 120
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Treatment options
Pathogen inactivation
Annexes
Page 8/8
Lime
Reference: Faecal Sludge Management for disaster Relief: Technology comparison study
CAPEX
OPEX
Whole life cost (10 years)
$975 per m3 treated
$9 per m3 treated
$396,870
Capacity
11 m3 per day

## Slide 121
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pathogen inactivation
Treatment options
Annexes
Reference: WHO - A guide to the development of on-site sanitation / R Franceys, J Pickford & R Reed
Pathogen inactivation
There is a variety of pathogen types found in wastewater and faecal sludge, each with different survival capacity
Ebola virus can also be found in urine, faeces and grey water
SARS-Cov-2 (causing the Covid-19 infection) can also be found in faeces, limited evidence in urine and potentially in grey water
Sullage = grey water
Page 1/4

## Slide 122
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pathogen inactivation
Treatment options
Annexes
Reference: NSW, Brown and Root Service, Septic Safe Onsite Sewage Risk Assessment System (OSRAS) handbook – Annex F
In salty water, vibrio cholerae can survive for months
It’s important to check if the treatment process effectively eliminate helminths eggs and cysts
Page 2/4
In fresh water, Ebola virus can survive for 6 days, while still unknow, tests have demonstrated the potential infection route through wastewater
Guidance from WHO states that the “Ebola virus is likely to inactivate significantly faster in the environment than enteric viruses with known waterborne transmission (e.g., norovirus, hepatitis A virus)”
Without treatment this is the number of day pathogens need to be contained to avoid contaminating water sources or people

## Slide 123
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pathogen inactivation
Treatment options
Annexes
Reference: NSW, Brown and Root Service – Septic Safe Onsite Sewage Risk Assessment System (OSRAS) handbook – Annex F
The most important factor affecting the survival of all helminth eggs is temperature, with rapid death resulting from temperatures below freezing and above 45°C (Feachem et al. 1983).
Inactivation of bacteria is done through competition with other microflora, desiccation and high temperature
Treatment processes such as composting and anaerobic digestion raise temperature up to 60 °C
Page 3/4

## Slide 124
Treatment
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Final disposal
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Pathogen inactivation
Treatment options
Annexes
Reference: NSW, Brown and Root Service, Septic Safe Onsite Sewage Risk Assessment System (OSRAS) handbook – Annex F
Temperature is the most predictor of virus inactivation.
Heat, high or low pH, sunlight (UV) and common disinfectants (such as chlorine) all facilitate the inactivation of human enteric virus
Page 4/4
Leaked into groundwater, the virus capacity to contaminate people will depend how long until it reaches any water point compare to the virus survival rate

## Slide 125
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Reuse
Burying
Pollution risks
The various treatment technologies generate different products whose quality and pollution risks will condition which disposal method is the safest for people’s health and the environment
For more information on standards for sludge and effluent reuse : WHO – WHO Guidelines for the safe use of wastewater, excreta and greywater in agriculture and aquaculture
Anaerobic digestate
Compost
Biomass (plant, bacteria, fish)
Biogas
Filtered effluent
Still contain pathogen above WHO recommended level for reuse
Still contain organic matter with biological oxygen demand high enough to disturb environment and water bodies
Dry sludge
High Carbon, Nitrogen and Phosphorus content
Vermicompost
The compost produced by the worms is sterile, but there is no guarantee it is free from pathogen as fresh faecal sludge can be mixed with the compost
Reference: A. Nigussie et al. – Vermicomposting as a technology for reducing nitrogen loss and greenhouse gas emission from small-scale composting
Participate in the reduction of greenhouse gas emissions

## Slide 126
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Burying
Disposed in a landfill mixed with solid waste
Time and cost saving: use existing infrastructure and reduce capital cost
Proper equipped landfills are waterproofed to protect groundwater
Subject to landfill operator approval
Can potentially cause instability in landfill cell slope
Fees to use the landfill need to be included into the OPEX
Disposed in a dedicated landfill (monofil)
Can be built near the treatment facility (reduce transport cost)
Designed to sludge specification
Construction licence can be included with the treatment plant’s
In clay soil simple trenches, easy to dig without heavy machinery are sufficient for burying the sludge
Construction and operation cost need to integrated into budget
Need space
Preparation period can take time as it includes soil and hydrogeological analysis prior to design
If clay is not available to waterproof the cells, geotextile not available in country may be required (longer procurement time)

## Slide 127
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Reuse
Page 1/3
The most widely reuse for faecal sludge & wastewater treatment products are soil conditioner and organic fertilizer
Soil conditioner
Organic fertilizer
Spread over plants to provide them with nutrients
Mixed with soil to improve its physical, biological and / or chemical structure in preparation for planting.
Different plants have different nutrient needs. How useful is the treated sludge as fertilizer will depend on its nutrient ratio for the main element Nitrogen, Phosphorus, Potassium, and other secondary element such as Calcium, Sulphur, etc.,
Clay + humus + Calcium
macropore
micropore
Silt
Sand
Aggregate
The addition of organic matter causes bacteria proliferation and stimulate roots development as well as increase the clay humus complex
Composts are the best form of soil conditioner – even better if the composting process combines sludge with plant debris
Assume that not all pathogens have been inactivated and avoid contact with any edible part of the plant
 Reuse is not appropriate for vegetable gardening such as lettuce!!!

## Slide 128
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Page 2/3
Fuel briquettes
After a process of carbonization, dry sludge mixed with carbonized biomass, such as saw dust and rice husks, can be moulded in briquettes
Gardening waste can be used as biomass and fuel for carbonization process
Adapted stoved improve fuel efficiency of the briquette
A kg of briquettes burns at the equivalent of 3 kg of charcoal
Buy-in and community engagement is required at the initial stages of developing the briquette manufacturing and marketing
Potential for income generation
Alternative to firewood collection, reducing both environment impact and risk to women
Sensitisation of communities on latrine proper use to improve faecal sludge quality

## Slide 129
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Reference: Feacal sludge management – Systems approach for Implementation and Operation
Page 3/3
Using deep trench row in tree plantation and only if the risk to groundwater pollution is very low
Other reuses
Irrigation (ensuring there is no contact with edible part of plants)
Aquifer recharge (provide the soil has time and capacity to remove the residual pollution)

## Slide 130
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Reference: ARGOSS 2001. Guideline for assessing the risk to groundwater from on-site sanitation – British Geological Survey Commissioned Report
Pollution risks
The principal concern for contamination from faecal sludge deposit, treatment product and effluent are pathogen and nitrate, with the later accumulating overtime with delayed pollution risks for water sources.
Page 1/3
Soil profiles, permeabilities of soil layers and groundwater levels must be analysed to evaluate the potential for pollution attenuation and groundwater pollution risks.
The smaller the pores and voids the slower leaching fluid travel through soil layers, increasing the potential for pollution attenuation
Significant risk - less than 25 days travel time
Low risk - between 25 and 50 days travel time
Very low risk - greater than 50 days travel time

## Slide 131
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Reference: ARGOSS 2001. Guideline for assessing the risk to groundwater from on-site sanitation – British Geological Survey Commissioned Report
Page 2/3
Sources of faecal pollution within urban and rural setting from a) sanitation and b) other sources
Unsaturated zone
First line of natural defence against groundwater pollution
Where the most effective pollution attenuation occurs
Biological activity in the upper soil layers can remove, transform, retard microbiological and to a lesser extent chemical contamination
Saturated zone
Pollution attenuation more limited,
Distance to water point from contamination entry zone and the speed of groundwater travel will condition the risk to human beings

## Slide 132
Final disposal
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Continuity of service
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Annexes
Burying
Reuse
Pollution risks
Reference: ARGOSS 2001. Guideline for assessing the risk to groundwater from on-site sanitation – British Geological Survey Commissioned Report
Page 3/3
Pollution attenuation processes within the saturated and unsaturated zones
Die-off of pathogen will depend on their survival time in various environment (from a few days for the cholera vibrion up to several months for helminths eggs in fresh water)
Pathogens’ diameter compared with aquifer matrix apertures
Mechanical filtration is more effective for larger organisms such as protozoan cysts and helminths but will also help to attenuate bacteria and is dependent on the pore size of the rock

## Slide 133
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Where there are human beings there is the need to ensure proper excreta disposal service for as long as the settlement lasts
While camps are temporary structures to provide immediate protection and assistance to refugees and internally displaced people, people length of stay vary widely from a few months to several decades in protracted crisis.
However, most people affected by a crisis are more likely to be hosted by local population or to move in urban or peri-urban locations often in abandoned buildings and / or flood prone areas
Each situation faces its own challenges to ensure any excreta disposal system continue to deliver quality service to all affected and hosting population.

## Slide 134
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Preparedness
Page 1/5
Emergency phases
What are the activities to implement and the parameters you need to check and verify in order to ensure an excreta disposal service is in place and operational in all phases of an emergency, whatever the settings?
What are the hazards that can / will affect excreta disposal services?
What are the hazards that can / will displace people to areas where there is no functional excreta disposal service?
e.g., flood can destroy latrines, treatment systems, damage transport trucks, overflow and fill latrines, damage water network and stop latrine flushing system, etc.
e.g., severe drought reduces access to water impacting the flushing of latrines and sewerage as well as handwashing, it can also dry out clays and undermine foundation of infrastructure
What are the population groups whose access to excreta disposal services will be the most affected?
Contingency planning exercises usually provide information on hazards, geographical areas and potential affected population size. But it often does not inform on how various population groups are affected differently by disaster.
Local disaster response plan may inform on location for evacuation centres (often schools) but not the status of its excreta disposal system neither if there is enough infrastructure to serve the number of affected population it can shelter.
What are the existing excreta disposal systems and their functional status? Has the markets for material and services been assessed?
It important to examine both what function and what doesn’t and why.
e.g., technical issues may reflect local entrepreneurs’ skills and limitations
Operation and maintenance issues may highlight service affordability limitation
Misuse and limit use should alert on design problem as well as security concern to access services and in general a lack of users’ consultation and preference inclusion for designing systems and infrastructures
What emergency latrine model is appropriate and what material should be pre-stocked or can standby agreement with suppliers / enterprises be made as preparedness planning?

## Slide 135
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Page 2/5
1st phase / onset emergency
Speed is important but not at the sake of quality and consultation with people
Build a good enough excreta disposal system for the first few weeks while you defined and build the final system based on a proper technical assessment and consultation, design with local actors
Tools and material supporting communities to manage open defecation
Container based latrine / PeePoo bag
Deep trench latrine (ratio 1:50)
Assess and strengthen existing Faecal Sludge collection and transport system
Set monitoring system
Where and who are the “invisible” people? What difficulties do they have to access excreta disposal services?
What are the enablers and blockers for sanitation uptake?
Urban
Rural
Camp
Sanitation stakeholders, construction and services delivery mapping
Gender sensitive excreta disposal services’ risk mapping and analysis
Train and implement SaniTweak for adaptation of latrine models
Set up / reactivate and train sanitation committee(s)
Where malnutrition has high prevalence, target families with malnourished children with sanitation package (latrine subsidy & hygiene promotion)
Train and support cleaning and repair teams
Anthropological / socio-economical study

## Slide 136
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
2nd phase / stabilisation period
Page 3/5
Building a sound and affordable operation and maintenance system is essential especially if the excreta disposal system will be needed for more than a year
Support upgrade up the sanitation ladder building from existing systems and practices
Ensure local authorities, utilities and technical department are involved in all steps of design and construction of excreta disposal services
Analyse capacity building needs of excreta disposal service actors
Construction of public institution latrines (school and health centres)
Distribution tool kits and material (slab) for household latrine construction
With local authorities, design and build faecal sludge treatment system when not existing
Voucher (material, technical human resource or artisan for full service) to vulnerable households for upgrade or construction of latrine
Build family shared latrine, lined and desludgeable (ratio 1:20)
Support local artisans to produce slab (tools and equipment, voucher for most vulnerable households)
Upgrade manual desludging service (manual pump, protection equipment, training)
Voucher for desludging service (vulnerable households, public institution)
Operators and monitors’ training need to be planned and implemented
Identify and support sanitation “champions” who will model and promote appropriate infrastructures and practices
Set up or hire local desludging service when existing (with a voucher system)
Support families with consumable and tools for cleaning and small maintenance
Maintain and equip repair team
With local authorities, design and build faecal sludge treatment system when not existing and if the type of latrine built requires it (N/A in case of tiger worm toilet or UDDT)
Support community health workers and local authorities (or sanitation committee) develop and implement a sanitation and handwashing promotion plan
“Cash for latrine” conditional grant
Urban
Rural
Camp

## Slide 137
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Recovery / exit phase
Page 4/5
Accompany people going back to their place with household level infrastructure, through participatory approaches and subsidies for the most vulnerable
Support local authorities, utilities and / or technical department take over the supervision or O&M of public infrastructures and services
Support local enterprises for appropriate materials and services market
With local authorities and local entrepreneur explore waste to value project (compost, biogas, irrigation) associated with treatment plant
Participative and community approach to manage ODF status
With communities explore and design low-cost ecological sanitation options (Arborloo, Fossa Alterna, adapted UDDT)
Support local entrepreneur for the construction of public toilet (combined with biogas as transitional storage / decentralised faecal sludge treatment station)
Identification of micro-finance institutions and support for project definition to access loan
Review excreta disposal service operational cost, identify options for minimising OPEX, collaborate with local utilities… and evaluate feasibility of transferring operation and maintenance management
Be careful of labour law and refugees’ status as not all staff can be transferred into utilities’ workforce
Transfer of service delivery responsibility is easier if the design and planning of the system was done with local authorities and within an overall sanitation plan
Implement required structural change to reduce OPEX, build capacity of local utility for transfer of management responsibilities
Communication and discussion with communities on the transfer plan (purpose, responsibilities, consequence, cost, etc.). Adapt plan with feedbacks.
Market evaluation for latrine construction material, faecal sludge treatment product
Market evaluation faecal sludge treatment product prospect
Urban
Rural
Camp

## Slide 138
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Prevention & mitigation
Page 5/5
Identify lessons learned from how disasters have impacted excreta disposal systems
Advocacy to improve designing, financing for resilient excreta disposal systems
If there isn’t a local sanitation strategic plan involving all stakeholders, how can the development process be initiated / supported?
Who are the sanitation champions?
Partnership with CSO for quality and access equity to sanitation service monitoring
Construction of privately managed public toilet in market, bus station located in cholera hotspots (associated with biogas / Faecal sludge deconcentrated treatment station)
Community capacity building to identify sanitation service needs and authorities influencing / advocacy
Support sanitation strategic and planning workshop at local and regional levels
Strengthen sanitation services in evacuation centres
Assess existing camp sanitation system capacity
Review past camp setting and management lessons learned
Whenever there is a contingency planning exercise planned, it’s important to read the various scenario with an excreta disposal service lenses:
What level of service will be needed, potentially for how long and where?
What did we do right before, what could we improve in the future?
How might we integrate lessons learned from previous emergencies in future responses?
How might we better involve communities and local authorities at all stages of setting up an excreta disposal service in an emergency?
How can the markets for sanitation material and services be supported during an emergency response?
Urban
Rural
Camp

## Slide 139
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Budgeting
Funding availability is often higher at a beginning of an emergency and therefore it’s important to plan carefully the various aspect of the excreta disposal system that need / can be funded in the first 6 months and later.
Community engagement
Page 1/4
Assessment
0-6 month
6-12 months
> 1 year
Preparedness
Monthly incentives for volunteers (1 woman, 1 man per 1,000 targeted people)
Community group grant (1 group per 5,000 targeted people)
Safe meeting area / Community centre
Communication / phone credit
Community mobilisation kits
Capacity building / training
Equipment and material for community events
Translation service
Formative research (anthropological, socio-economical studies)
Kit (Tablet, software, stationaries)
People cost (Incentive, perdiem, accommodation, etc.)
or

## Slide 140
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Page 2/4
Latrines
0-6 month
6-12 months
> 1 year
Preparedness
Rehabilitation / construction Institutional latrines (school / health centre)
Emergency latrines
Tool kit for communities
Voucher / subsidies for slab and other latrine material
Support to local entrepreneur producing slab / latrine walls
Sanitation market evaluation
Latrine cleaning kit
CLTS triggering and monitoring cost
Fully subsidised, adapted household latrine (e.g. UDDT)
Desludging
Desludging kit
Desludging service cost (people, consumable or rental desludging truck)
Transitional storage and transport (material and service operation cost)
If renting the service of a desludging truck, both lines are included in the same service

## Slide 141
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Treatment / disposal
Page 3/4
0-6 month
6-12 months
> 1 year
Preparedness
Operation and maintenance
Rehabilitation / replacement of latrines
Repair team / material cost
Cleaning team people cost (salaries, incentives, etc.)
Treatment site cost (salaries / incentives, consumable and tools, etc.)
Rehabilitation wastewater / Faecal Sludge (FS) treatment plant
Construction wastewater / FS treatment plant
Support micro-business with biodigester / composting treatment products
Market survey for recycling / use of treatment products
Piloting innovative treatment technique
Piloting project creating synergy between FS treatment & farming

## Slide 142
Continuity of service
Modalities of implementation
Adaptation for easier access
Latrine superstructure
Slab
Storage / pre-treatment pit
Desludging
Treatment
Final disposal
Operation & maintenance
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Budgeting
Annexes
Emergency phases
Monitoring
Page 4/4
0-6 month
6-12 months
> 1 year
Preparedness
Other budgeting post
Logistic cost (transport and storage of material + vehicle for staff movement)
Staff salaries (1 assistant officer per 5,000 targeted people if direct implementation, or 10,000 people if construction is done through enterprise + 1 officer for 2-4 assistant + PHE manager)
Trainings, conference, other meeting cost
Support to local authorities’ sanitation strategic plan development
Perdiem, accommodation and transport cost for government / university sanitation specialist collaboration
Complain and feedback mechanism
Tools & equipment (Camera, GPS, protective gear, sticks, etc.)
Kit (Tablet, software, stationaries)
People cost (Incentive, perdiem, accommodation, etc.)
Decommissioning sanitation infrastructures (cleaning, disinfecting, dismantling, closing safely)

## Slide 143
Tiger worm
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Cost comparison
WASH committee
WASH utility
Annexes
CAPEX
OPEX 1 year
Some sanitation infrastructure with low capital expenditure (CAPEX) have high operational expenditure (OPEX). For situation where excreta disposal infrastructures are needed long term (>1-2 year) it is important to aim for low OPEX even if the CAPEX is high, especially since higher funding are usually available at the beginning of an emergency and shrink afterward
Cost covered by Users, Community engagement, staff, logistic and overhead not included
20,000 USD
1,000
2,000
3,000
4,000 USD
10,000
5,000
Centralised treatment
Decentralised treatment
Latrine
Upflow filter
Geotubes
Biogas
ABR
Anaerobic lagoon
Unlined emergency Latrine
lined permanent Latrine 50p
lined permanent Latrine 20p
Raised Latrine 20p
Ecosan / UDDT
Lime
200,000

## Slide 144
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Cost comparison
WASH committee
WASH utility
Annexes
Cost comparison
UDDT $ 1,070
TWT $ 570
Household level
Emergency unlined pit latrine (public)
CAPEX $ 44
Masonry and CGI Raised pit latrine
$ 220
(family shared)
Decommissioning and closing pit after 2-3 month
Yearly OPEX $ 96
Build a new latrine to continue the service
Yearly OPEX $ 234
Manual emptying once a year manageable by users
Tiger worm toilet
$ 310
(family shared in camp setting)
Full excreta disposal cycle considered for the cost comparison of systems
Manual emptying once every 5 years
Yearly OPEX $ 3
Centralised Treatment
Yearly OPEX $ 0.1 to 1.8
Shared CAPEX $ 1.9 to 65
Transport & reuse
Cost recovery with sale product OPEX $ 0
Transport and bury manageable by users
Transport and reuse manageable by users
Calculation parameters: cost equivalent to 20 people, faecal sludge accumulation rate 100 litres per person and per year, 1 cubicle shared by 50 people for public latrine, 20 people for family shared latrine and 5 people for household level. Mechanical desludging is optimised (1 trip empties several latrines until full).
Procurement cost are based on Asia prices and will varies for other regions. E.g., for Ethiopia, CAPEX is increased by 80 to 100% with similar labour cost, while in South Sudan construction cost are multiply by 4.5 and labour cost are divided by 5.
Clean and repair
Yearly OPEX $ 2,800
Masonry lined pit latrine $ 446
(family shared)
Manual desludging
Yearly OPEX $ 60
Mechanical desludging with transport
Yearly OPEX $ 10 for lined pit
$ 36 for raised pit
Transitional storage and transport
Yearly OPEX $ 12
Decentralised Treatment
Yearly OPEX $ 0.1 (Biogas) to $ 20 (Lime)
Shared CAPEX $ 4 to 112 (nber year operate, type)
Transport & bury
Yearly OPEX $ 4
Clean and repair
Managed by users (labour and consumable)
Clean and repair
Managed by users with provision consumable
Yearly OPEX $ 315
Page 1/3
Assuming people are willing to pay enough to cover the transport cost
Amounts are indicative and do not include any costs related to community engagement, hygiene promotion, and organisation staff.

## Slide 145
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Cost comparison
WASH committee
WASH utility
Annexes
Page 2/3
Cost for 20 people over 10-year period according to phasing scenario
Scenario # | Description | Total cost | Comment
1 - camp setting | Emergency unlined pit latrine and replacement | $ 31,344 | Supposed sufficient space to build new latrines. Most likely a lack of buy-in and collaboration from users
2 - camp setting | Emergency unlined pit latrine for 6 months then permanent lined pit latrine family shared, sludge transported and disposed in a landfill | $ 4,568 | For planning purpose consider 2m3 of sludge per year for 20 people instead of 0.8 m3 after treatment. If the water table is high and the pit must be raised, then the volume to evacuate per year is above 7m3. Supposed the existing landfill (if any) is accepting the sludge*
3 – camp setting | Emergency unlined pit latrine for 6 months then permanent lined pit latrine family shared, sludge transported and disposed in a landfill for 6 month while a treatment system is built Starting year 2 all sludge is treated before transported in landfill | $ 4,992 | 0.8 m3 per 20 people per year more susceptible to be accepted by landfill (dryer and less instability risks). *
4 – camp setting | Emergency unlined pit latrine for 6 month then Tiger worm toilet family shared | $ 4,852 | 
5- host community | Support for the construction of UDDT or Tiger Worm Toilet at household level | $ 570 (TWT) or $ 1070 (UDDT) | If in a camp setting, then a 6 months phase with emergency latrine may be needed (with an additional cost of about $ 1,600)
*A landfill fee per m3 may apply and is not included in the total cost (landfill operation cost average is $ 35 per tonne)
10% of the cost in the first year
About 50% of the cost in the first year
100% of the cost in the first year

## Slide 146
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Cost comparison
WASH committee
WASH utility
Annexes
Page 3/3
Options / Types of latrine | Suitability of option | Costs (Asian reference) |  |  |  | Comments on calculation OPEX | Treatment associated costs (10 years)
 |  | CAPEX | OPEX | Total 10 year | Total 20 year |  | 
Simple Pit Latrine – Pour flush – unlined – movable superstructure (wood and bamboo mat) | Area with stable soil and enough space to dig new pit. Best when good infiltration rate | $ 150 | $ 55 + $ 46 | $ 306 | $ 462 | Dig a new pit (~1-1.5m3) and move superstructure every 5 years. Change bamboo mats every 10 years | N/A
Simple Pit Latrine – Pour flush – lined - superstructure (wood and bamboo mat) | Suitable when desludging service is available and affordable | $ 185 | $ 30 + $ 46 | $ 291 | $ 397 | Desludged every 5 years. Change bamboo mats every 10 years | $ 0.5 (ABR), $ 1.1 (Biogas), $ 13 (upflow filter)
Raised Latrine – Brick / CHB masonry | Area with high water table. Need more frequent desludging (at least 5-6 time more). Shower should be separated. Suitable when desludging service is available and affordable | $ 225 | $ 30 | $ 525 | $ 825 | Desludged once a year | $ 1.2 (ABR), $ 2.7 (Biogas), $ 32 (upflow filter)
UDDT – double chamber CHB masonry, superstructure CGI sheet | Area difficult to dig, high water table or with high risk of groundwater contamination. Suitable for long term | $ 268 | $ 15 + $ 110 | $ 418 | $ 678 | Empty one chamber once a year. Change CGI sheet after 20 years | N/A
Tiger Worm Toilet – stone and brick masonry, CGI sheet | Above or below ground, detergent should not be used, and shower should be separated | $ 285 | $ 10 + $ 110 | $ 385 | $ 595 | Empty vermicompost every 5 years. Change CGI sheet after 20 years | N/A
Septic Tank | Require space for effluent percolation or connection to sewer | $ 850 | $ 50 | $ 1,000 | $ 1,150 | Desludged every 3 years (depending on the designed sludge accumulation volume) | $ 0.4 (ABR), $ 0.8 (Biogas), $ 9.5 (upflow filter)
Estimated cost for 1 household (5 people) for building and maintaining a toilet
Cleaning cost not included

## Slide 147
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
WASH committee
Cost comparison
WASH utility
Annexes
WASH committee
Transparency
The more community members understand the project in terms of finances, committee functioning and selection of committee members, the more chance of success
Inclusion
Active involvement of women and other vulnerable groups, and fair representation of different ethnic groups
Participation
Meaningful community input at the program design stage clarify which activities are the responsibility of communities’ members
Ownership
It’s a community committee. Terms of reference, members selection, committee structure, constitution, etc., should be devised and agreed with the wider community
Incentives or no incentives?
Be consistent to what is casual work, volunteer works without incentive and works with incentives (within the organisation and other organisations). What the labour law says?
Committee members’ need also to earn their living and deal with domestic duties
Explore feasibility of community-based solution to compensate committee members’ time
Built from existing structures whenever possible
Capacity building
Training needs should be developed in collaboration with the community to ensure materials are appropriate and to encourage participation
Accountability
2-way communication and timely response to community concerns and delivery of commitments within an agreed timescale and accountable to local authorities or village leader

## Slide 148
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
WASH utility
Cost comparison
WASH committee
Annexes
WASH utility / private contractor with a service agreement
The legal definition can vary between countries according to the type of organisation legally accepted for operating, controlling, managing and / or owning a WASH public service and its infrastructures.
There is sometime a minimum population target for an organisation to be defined as “utility”. Below this target, community structures such as Users’ association or WASH committee are in charged of the WASH service
In which conditions is it preferable to works through WASH utility to set up and manage an excreta disposal system in an emergency setting?*
Page 1/2
What is the cost recovery scheme?
What is the population willingness to pay for the service?
How much it cost to operate and maintain for the WASH utility?
What is the WASH utility capacity to operate and maintain the service?
How much do communities trust their WASH utility?
* There is no clear-cut answer to this question and more testing and research are required to understand success and failure conditions

## Slide 149
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Operation & maintenance
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
WASH utility
Cost comparison
WASH committee
Annexes
Page 2/2
Fragmented sector and multiplicity of actors
Lack of comprehensive sanitation plan connecting sewer, onsite sanitation, faecal sludge transport and treatment systems
Legal structure and registered
More attractive for staff long term job opportunity
Handover to an existing utility requires buy-in both from the utility team (acceptable incurred cost, technicity and technical expertise, infrastructure in good enough condition) and from the users / community (trust that the level of service will be maintained, understanding new roles and responsibility, willingness and ability to pay for the service cost)
Tentation to focus on paying customer and concentrate OPEX on zones with highest cost recovery potential
Better connection to local authorities and local market
Governance and lack of transparency are recurrent issues with utilities
Education focus on construction and less on operation and maintenance skills
Staff experience with operation and maintenance issues
Preventative maintenance and capital maintenance rarely integrated in budget and operation plans
Need for a transition plan to accompany users from a fully subsidised to paid service
Exit plans involving WASH utilities need to be done from the design stage with the participation of local authorities and the utility
In refugee camp settings, the legal status of refugee may impact the transfer of staff to a water/sanitation utility

## Slide 150
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Double door pit latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Emergency sandbag raised latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
UDDT double vault
Drawing
BoQ
This design is from the Philippines 2007/2014 in Evacuation Centers with limited space
Off-set pour-flush latrine
Containment pour flush latrine
Tiger worm toilet
Double door pit latrine

## Slide 151
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Double door pit latrine
IN | Item descriptions | Unit | Qnty | Cost/Unit | Total cost
1 | Pit Digging | m3 | 2.4 |  | 
2 | Coco Lumber 1"x2"x8' | pcs | 22 |  | 
3 | Coco Lumber 2"x2"x10' | pcs | 16 |  | 
4 | Coco Lumber 2"x3"x8' | pcs | 6 |  | 
5 | CWN 2" | kg | 2 |  | 
6 | CWN 3" | kg | 2 |  | 
7 | CWN 4" | kg | 2 |  | 
8 | Barrel Bolt (Ordinary) | pcs | 2 |  | 
9 | Hinges 3"x3" | pair | 4 |  | 
10 | Door Handle 5" | pcs | 2 |  | 
11 | PVC Pipe 2" dia.(Sanitary Pipe) | pcs | 1 |  | 
12 | Latrine Slab w/ P-Trap | set | 2 |  | 
13 | Tarpaulin 4x6 | shits | 2 |  | 
14 | Labour cost for construction |  |  |  | 
15 | Skilled | Man-days | 2 |  | 
16 | Un- skilled | Man-days | 4 |  | 
 | Total Cost Per Country (Local Currency): |  |  |  | 
BoQ for Diagram/drawing -I- Double Door Communal/Shared Simple Pit Latrines (unlined and non-ventilated)
IN | Item descriptions | Unit | Qnty | Cost/Unit | Total cost
1 | 2"x2"x6' Wood baton | pcs | 9 |  | 
2 | Zinc/iron Sheet G26X 1.8cm, 3mL | pcs | 2 |  | 
3 | CWN 2", 1 1/2" | kg | 0.5 |  | 
4 | un- skilled labour | Person/day | 2 |  | 
 | Total cost per Country (Local Currency): |  |  |  | 
Additional cost for lining the pit
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 152
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Deep Trench latrine
BoQ
Drawing
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
A Deep Trench Latrine is a widely used as communal latrine option for emergencies. It can be quickly implemented (within 1–2 days) and consists of several cubicles aligned up above a single trench. A trench lining can prevent the latrine from collapsing and provide support to the superstructure
Tiger worm toilet
Deep Trench latrine
Emergency sandbag raised latrine

## Slide 153
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Deep Trench latrine
Drawing
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Internal lining can be done using sand bag or locally avail be material for Emergency purpose
BoQ
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 154
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
IN | Item descriptions | Unit | Qnty | Cost/Unit | Total cost
 | Sub Structure |  |  |  | 
1 | Excavation/Pit Digging 3m deep | m3 | 14 |  | 
2 | Sand Bags for Internal wall lining | Pcs | 156 |  | 
 | Super Structure (+Floor Work) |  |  |  | 
3 | Timber Post 3"x2"x8' | pcs | 22 |  | 
4 | Timber 2"x1"x10' | pcs | 24 |  | 
5 | Timber 2"x2"x8' hand washing stand | pcs | 2 |  | 
6 | Timber Plank 10”x1”x6’ | pcs | 1 |  | 
7 | Nails 2" | kg | 1 |  | 
8 | Nails 3" | kg | 1 |  | 
9 | Hand washing plastic barrel/bucket with faucet – 20/30 ltrs | pcs | 1 |  | 
10 | Tarpaulin 4x6m (Plastic sheeting) | M2 | 33 |  | 
11 | Oxfam Plastic Slab (1.2x0.8) | Pcs | 4 |  | 
12 | Door Hinges | Pcs | 8 |  | 
13 | Door Locks(Internal) | pcs | 4 |  | 
14 | Sand Bags to protect the wall/pit from flush/flood water from | Pcs | 45 |  | 
 | Labour cost for construction |  |  |  | 
15 | Skilled | man-days | 4 |  | 
16 | Un- skilled | man-days | 8 |  | 
 | Decommissioning of Trench latrine |  |  |  | 
17 | Hydrated/chlorinated lime | kg | 10 |  | 
18 | Unskilled labour | Man days | 4 |  | 
 | Total Cost |  |  |  | 
BOQ for Diagram/Drawing ID 2 Deep Trench Latrine;( 3 M deep below NGL)
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 155
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Emergency desludgeable lined pit latrine
Deep Trench latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Tiger worm toilet
Emergency desludgeable lined pit latrine
Emergency sandbag raised latrine

## Slide 156
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Raised “trench” latrine
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Tiger worm toilet
Raised “trench” latrine
Emergency sandbag raised latrine

## Slide 157
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Raised “trench” latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
IN | Item descriptions | Unit | Qnty | Cost/Unit | Total cost
 | Sub Structure (+Block Work) |  |  |  | 
1 | Excavation of pit hole | M3 | 2 |  | 
2 | Hollow Concrete Blocks, 40x20x20 | pcs | 165 |  | 
3 | Cement Portland 50kg | bags | 6 |  | 
4 | Sand | m3 | 0.5 |  | 
5 | Gravel | m3 | 0.5 |  | 
6 | 10mm RC bar 12m length | pcs | 4 |  | 
7 | Binding wire | kg | 1 |  | 
8 | Wooden pole for formwork | pcs | 2 |  | 
9 | Timber 200x25mm for formwork | m | 12 |  | 
 | Super Structure |  |  |  | 
10 | CGI sheet 2m length | pcs | 10 |  | 
11 | Timber 100x50mm | m | 16 |  | 
12 | Timber 50x50mm | m | 8 |  | 
13 | Timber 50x25mm | m | 36 |  | 
14 | 75mm pvc vent pipe | m | 3 |  | 
15 | Nails (assorted 3" and 4") | kg | 6 |  | 
16 | Roofing nails | kg | 3 |  | 
17 | Hinges | pcs | 4 |  | 
18 | Door lock (inner) | pcs | 2 |  | 
19 | Door lock (outer) | pcs | 2 |  | 
 | Labour Cost |  |  |  | 
20 | Labour skilled(Mason Carpenter) | Man days | 6 |  | 
21 | Labour unskilled | Man days | 18 |  | 
 | Total Estimated cost |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 158
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Emergency sandbag raised latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 159
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Single pit latrine
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
20
–40
cm
10
cm
250-300cm
Support sand bag /Mason/ring
slab raised to stop water from
entering the pit
Tiger worm toilet
Emergency sandbag raised latrine
Single pit latrine

## Slide 160
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Single pit latrine
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
BoQ
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 161
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Single pit latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
IN | Item descriptions | Unit | Qnty | Cost/Unit | Total cost
 | Sub-Structure |  |  |  | 
1 | Excavation of 3m deep pit (Circular with R=0.6) | M3 | 3.5 |  | 
2 | Sandbag for Top soil lining (40-50 cm high) |  |  |  | 
3 | Mason work for top Pit lining (40 cm high)(Optional) (for slab support) | M3 | 0.7 |  | 
 | Super Structure(+ Floor Work) |  |  |  | 
4 | Plastic Slab (Oxfam type) | Pcs | 1 |  | 
5 | Domslab or concrete rectangular slab (Optional )( See details of the slab design and material required @ the last page ) | Pcs-1 |  |  | 
6 | Tarpaulin 4x6m (Plastic sheeting) for Walling and Roofing | M2 | 10 |  | 
7 | Corrugated Iron Sheet (GI34) for Walling & Roofing (Optional for instead of Plastic) | pcs | 9 |  | 
8 | Heavy wood columns (10cmx3m length)?? | pc | 6 |  | 
9 | Wood timber (2.5cmx5cmx4m)?? | pcs | 8 |  | 
10 | Nails 2’’ | kg | 1 |  | 
11 | Nails 3’’ | kg | 0.5 |  | 
12 | Roofing Nails | kg | 1 |  | 
13 | Door Hings | pcs | 2 |  | 
14 | Door Locks (Tower Bolts)(in &out side) | pcs | 2 |  | 
 | Labour Cost |  |  |  | 
15 | Skilled Labour | Man/days | 2 |  | 
16 | Non Skilled labour | Man/days | 6 |  | 
 | Total cost |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 162
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Raised Single pit latrine
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Tiger worm toilet
Emergency sandbag raised latrine
Raised single pit latrine

## Slide 163
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Raised Single pit latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
IN | Description | Unit | QTY | Unit cost | Total Cost
1 | Wooden Posts (4m x 5cm x 5cm) | Pcs | 16 |  | 
2 | Wooden Planks (4m x 20cm x 2.5cm) | Pc | ½ |  | 
3 | Nails (10cm Galvanized) | Kg | ½ |  | 
4 | Domed Head Nails (4cm Galvanized) | Kg | ½ |  | 
5 | Domed Latrine Slab (150cm dia x 5cm) | Pc | 1 |  | 
6 | Bricks (8cm x 12cm x 25cm) | Pcs | 54 |  | 
7 | Plastic Sheeting | M2 | 16 |  | 
8 | Metal Bolts and Washers (M10 x 12cm) | Pcs | 12 |  | 
9 | Metallic Door Bolt (4cm Galvanized) | Pc | 1 |  | 
10 | Metallic Padlock with 4 Sets of Keys | Pc | 1 |  | 
11 | Metallic Door Hinge (4cm x 8cm x 2mm Galvanized) | Pcd | 3 |  | 
12 | Wooden Grab Rails and Door Handles (Minimum 50cm Length) | Pcs | 4 |  | 
13 | Mirror (80cm x 60cm) | Pc | 1 |  | 
14 | Coarse Sand | M3 | 0.4 |  | 
15 | Coarse Gravel (6mm – 10mm) | M3 | 0.8 |  | 
16 | Cement (50kg sacks) | sack | 6 |  | 
 | Total Cost |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 164
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Off-set pour-flush latrine
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Tiger worm toilet
Emergency sandbag raised latrine
Offset pour-flush latrine

## Slide 165
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Off-set pour-flush latrine
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Reference: WEDC – Pour-Flush Latrines booklet
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 166
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
SaTo Pan Pour Flush Toilet
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
Containment pour flush latrine
UDDT double vault
Double door pit latrine
Diagram/Drawing -- SaTo Pan Pour Flush Toilet (Unlined/Lined/Raised – require adjustment on the BoQ once decided which one to adopt) (Option C)
Tiger worm toilet
Emergency sandbag raised latrine
SaTo Pan pour-flush toilet

## Slide 167
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
SaTo Pan Pour Flush Toilet
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
Containment pour flush latrine
UDDT double vault
Double door pit latrine
IN | Description | Unit | QTY | Unit cost | Total Cost
1 | Wooden Posts (4m x 5cm x 5cm) | pcs | 16 |  | 
2 | Wooden Planks (4m x 20cm x 2.5cm) | pcs | ½ |  | 
3 | Nails (10cm Galvanized) | kg | ½ |  | 
4 | Domed Head Nails (4cm Galvanized) | kg | ½ |  | 
5 | Domed Latrine Slab (150cm dia x 5cm) | pc | 1 |  | 
6 | Bricks (8cm x 12cm x 25cm) | pcs | 54 |  | 
7 | Plastic Sheeting | M2 | 16 |  | 
8 | Metal Bolts and Washers (M10 x 12cm) | pcs | 12 |  | 
9 | Metallic Door Bolt (4cm Galvanized) | pc | 1 |  | 
10 | Metallic Padlock with 4 Sets of Keys | pc | 1 |  | 
11 | Metallic Door Hinge (4cm x 8cm x 2mm Galvanized) | pcs | 3 |  | 
12 | Wooden Grab Rails and Door Handles (Minimum 50cm Length) | pcs | 4 |  | 
13 | Mirror (80cm x 60cm) | pc | 1 |  | 
14 | Coarse Sand | M3 | 0.4 |  | 
15 | Coarse Gravel (6mm – 10mm) | M3 | 0.8 |  | 
16 | Cement (50kg sacks) | sack | 6 |  | 
 | Total Cost |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 168
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Containment Pour flush latrine
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
UDDT double vault
Double door pit latrine
Example for a 2-door unit of contained pour flush latrines in a displacement camp, Philippines 2010.
Tiger worm toilet
Emergency sandbag raised latrine
Containment pour-flush latrine

## Slide 169
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Drawing
BoQ
Containment Pour flush latrine
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
UDDT double vault
Double door pit latrine
IN | Item descriptions | Unit | Qnty | Unit Cost | Total Cost
 | Material Required |  |  |  | 
1 | Timber (100x50x3600)L | pcs | 12 |  | 
2 | Timber (50x50x2400) | pcs | 11 |  | 
3 | Timber (50x25x2400) | pcs | 11 |  | 
4 | Timber Planks (225x20x2400) | pcs | 4 |  | 
5 | CGI Sheet (partition) 34G, 6’H | no | 1 |  | 
6 | CGI Sheet (door) 32G, 6’H | no | 3 |  | 
7 | CGI Sheet (roof), 32G, 8’H | no | 4 |  | 
8 | PVC Pipe, 100 mm - T250 | ft | 12 |  | 
9 | PE Tank 1000L | no | 2 |  | 
10 | Squatting slab with bend & pan (Oxfam) | set | 2 |  | 
11 | Silicon Gel (gum) | set | 1 |  | 
12 | Nails 3” | kg | 1 |  | 
13 | Nails 2” | kg | 0.5 |  | 
14 | Nails 1 ½” | kg | 0.25 |  | 
15 | Umbrella Nails 1 ½” | kg | 0.5 |  | 
16 | T-Hinges (150mm) | no | 4 |  | 
17 | Door handle (150mm) | no | 2 |  | 
18 | Tower Bolt (150mm) | no | 2 |  | 
19 | Gate hook (100mm) | no | 2 |  | 
 | Labour: |  |  |  | 
21 | Skilled labourer | man-day | 2 |  | 
22 | Un-skilled labourer | man-day | 4 |  | 
 | Total cost |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 170
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
UDDT double vault
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
Double door pit latrine
Tiger worm toilet
Emergency sandbag raised latrine
UDDT double vault

## Slide 171
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
UDDT double vault
BoQ
Drawing
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
Double door pit latrine
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 172
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Double door pit latrine
Off-set pour-flush latrine
Containment pour flush latrine
Drawing
BoQ
UDDT double vault
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
IN | Item description | Qty | Unit | Unit cost | Total cost
 | Vault Construction |  |  |  | 
1 | Cement | 4.5 | 50kg bags |  | 
2 | Sand | 0.6 | m3 |  | 
3 | Gravel 0.1 | 0.25 | m3 |  | 
4 | Hollow Concrete Blocks, 40x20x20 | 100 | pc |  | 
5 | PPR Pipe 50mm | 2 | metres |  | 
6 | PPR Elbow 50mm | 2 | pc |  | 
7 | Vault Doors | 2 | pc |  | 
 | Main Slab & Urine Pot |  |  |  | 
8 | Cement | 2.5 | 50kg bags |  | 
9 | Sand | 0.5 | m3 |  | 
10 | Gravel 0.25 | 0.5 | m3 |  | 
11 | Reinforcement bar, Ø6mm | 10 | kg |  | 
12 | Binding Wire | 0.5 | kg |  | 
13 | Bonda Iron | 2 | kg |  | 
14 | Purlin 5 x 7 x 400 cm, for slab form work. | 0.1 | pc |  | 
15 | PPR Pipe, Ø50mm | 0.1 | metres |  | 
16 | Floor Drain | 1 | pcs |  | 
 | Superstructure |  |  |  | 
17 | Eucalyptus pole Ø10cm | 6 | pc |  | 
18 | Eucalyptus pole Ø8cm | 6 | pc |  | 
19 | Purlin 5 x 7 x 400 cm | 3 | pc |  | 
20 | Timber 150 x 20 x 400cm | 1 | pc |  | 
21 | Engine Oil | 2 | litres |  | 
22 | Hollow Concrete Blocks, 40x15x20 | 40 | Pcs |  | 
23 | cement | 1 | bag |  | 
24 | sand | 0.5 | m3 |  | 
25 | Bamboo with standard length of 4m | 120 | pc |  | 
26 | plastic sheet | 0.5 | pc |  | 
27 | Iron sheet, 2 x 0.9 m, G-35, for roof and Door. | 4 | pc |  | 
28 | Nails, Roofing | 1.8 | kg |  | 
29 | Nails 10, cm | 2 | kg |  | 
30 | Nails, 6cm | 2 | kg |  | 
31 | Nails, 8cm | 1 | kg |  | 
32 | Tower Bolt,15cm | 2 | pcs |  | 
33 | Door Latch | 2 | pcs |  | 
34 | Butt Hinge, 15cm | 2 | pcs |  | 
35 | Pad Lock | 1 | pcs |  | 
36 | Hand Washing stand |  |  |  | 
37 | Eucalyptus Pools Ø 8cm 5 m long (for Truss/wall work) | 1 | No |  | 
38 | Hollow Concrete Blocks, 40x40x20 | 2 | pc |  | 
 | GRAND TOTAL COST FOR updated UDDT design |  |  |  | 
Tiger worm toilet
Emergency sandbag raised latrine

## Slide 173
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
BoQ
Design
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
Double door pit latrine
UDDT double vault
Tiger worm toilet
Reference: Tiger worm toilet manual
Emergency sandbag raised latrine
Tiger worm toilet (TWT)

## Slide 174
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
BoQ
Design
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
Double door pit latrine
UDDT double vault
Tiger worm toilet
Reference: Tiger worm toilet manual
Emergency sandbag raised latrine

## Slide 175
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
BoQ
Design
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
Off-set pour-flush latrine
SaTo Pan Pour Flush Toilet
Containment pour flush latrine
Double door pit latrine
UDDT double vault
Tiger worm toilet
Reference: Tiger worm toilet manual
Emergency sandbag raised latrine

## Slide 176
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Double door pit latrine
Off-set pour-flush latrine
Containment pour flush latrine
Design
BoQ
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
UDDT double vault
Tiger worm toilet
Emergency sandbag raised latrine
Sr.No. | Description | Quantity | Unit | Unit cost | Total
 | Material |  |  |  | 
1 | Hard wood 3" x3" post 9' length | 4 | pcs |  | 
2 | 3" x 2" hard wood 12' length | 9 | pcs |  | 
3 | 3"x1" hard wood 12' length | 2 | pcs |  | 
4 | 3" x 0.5" hard wood for beading | 9 | pcs |  | 
5 | 6" x 1" plank 12 length | 5 | pcs |  | 
6 | pan cover with 5 ply wood , 2" x1" frame | 1 | pcs |  | 
7 | 1"x 1" wire mesh | 0.04 | roll |  | 
8 | concrete footing with M.S flat ( 8" x 1' x 1.5') | 4 | pcs |  | 
9 | concrete ring ( 3' dia, 1.5' height) | 2 | pcs |  | 
10 | reinforced concrete cover with man hole (3' dia) | 1 | pcs |  | 
11 | vernish ( 1 gal ) | 1 | gal |  | 
12 | cement | 0.76 | bags |  | 
13 | boulder | 0.125 | sud |  | 
14 | Aggregate | 0.038 | sud |  | 
15 | sand | 0.019 | sud |  | 
18 | brush | 2 | pcs |  | 
19 | GI plain sheet ( 5 ft ) | 30 | ft |  | 
20 | C.G.I roofing sheet | 2 | pcs |  | 
21 | roofing nail | 0.5 | viss |  | 
22 | nail ( various size) | 1 | viss |  | 
23 | 1/2" dia Bolt and Nut 5" long with washers | 8 | pcs |  | 
24 | pan | 1 | pcs |  | 
25 | 3" dia PVC pipe 4' | 1 | nos |  | 
26 | tarpaulin sheet 4' x 4' | 0.04 | roll |  | 
28 | fly screen 4' x 5' | 5 | ft |  | 
29 | 4" Hinge | 3 | pcs |  | 
30 | 4" Handle | 2 | pcs |  | 
31 | tower bolts | 2 | pcs |  | 
32 | bedding material/coconut coir | 5 | bags |  | 
 | Labour cost |  |  |  | 
33 | carpenter | 2 | man.days |  | 
34 | mason | 1 | man.days |  | 
35 | worker | 4 | man.days |  | 
 | Total |  |  |  | 
Single door household TWT

## Slide 177
Latrine superstructure
Storage / pre-treatment pit
Treatment
Continuity of service
Annexes
Modalities of implementation
Adaptation for easier access
Slab
Desludging
Final disposal
Consultation
Excreta disposal system
Assessment
Monitoring
Main page
Operation & maintenance
Double door pit latrine
Off-set pour-flush latrine
Containment pour flush latrine
Design
BoQ
Deep Trench latrine
Emergency desludgeable lined pit latrine
Raised “trench” latrine
Single pit latrine
Raised Single pit latrine
SaTo Pan Pour Flush Toilet
UDDT double vault
Tiger worm toilet
Emergency sandbag raised latrine
Sr.No. | Description | Quantity | Unit | Unit cost | Total
 | Material |  |  |  | 
1 | Hard wood 3" x3" post 9' length | 6 | pcs |  | 
2 | 3" x 2" hard wood 12' length | 15 | pcs |  | 
3 | 3"x1" hard wood 12' length | 3 | pcs |  | 
4 | 3" x 0.5" hard wood for beading | 13 | pcs |  | 
5 | Pan cover with 5 ply wood , 2" x1" frame | 2 | pcs |  | 
6 | 8mm rebar | 240 | Rft |  | 
7 | 6 mm rebar | 160 | Rft |  | 
8 | Binding wire | 0.5 | viss |  | 
9 | vernish ( 1 gal ) | 1 | gal |  | 
10 | cement | 22.34 | bags |  | 
11 | boulder | 3.225 | sud |  | 
12 | Aggregate | 0.25 | sud |  | 
13 | sand | 1 | sud |  | 
15 | brush | 2 | pcs |  | 
16 | GI plain sheet ( 5 ft ) | 55 | ft |  | 
17 | C.G.I roofing sheet | 4 | pcs |  | 
18 | roofing nail | 1 | viss |  | 
19 | nail ( various size) | 1.5 | viss |  | 
20 | 1/2" dia Bolt and Nut 5" long with washers | 12 | pcs |  | 
21 | pan | 2 | pcs |  | 
22 | 3" dia PVC pipe 4' | 2 | nos |  | 
24 | fly screen 4' | 15 | ft |  | 
25 | 4" Hinge | 6 | pcs |  | 
26 | 4"handle | 4 | pcs |  | 
27 | tower bolts | 2 | pcs |  | 
28 | padlock | 2 | pcs |  | 
29 | Bedding material/coconut coir | 25 | bags |  | 
 | Labour |  |  |  | 
30 | Carpenter | 2 | man.days |  | 
31 | Mason + steel fixer | 5 | man.days |  | 
32 | Worker | 8 | man.days |  | 
 | Total |  |  |  | 
Double door shared TWT